## 60K ID
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date |  | 5/31/2023 11:21:02 AM
Test Method |  | Heating |  |  | File Name |  | P-20230531 09-07-23.psy
Rated Capacity |  | 0 W |  |  | ID Model Name |  | 2Kw 10cmm
Rated Power |  | 2,000 W |  |  | ID Serial Number
Power Source |  | 3P3W / 108 V / 0 Hz |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  | R22 - g |  |  | Exp. Device
ID Entering DB/WB |  | 20 / 15 ℃ |  |  | OD Entering DB/WB |  | 29 / 19 ℃
- |  |  |  |  | -
Note
2kw 10cmm heatloss check
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | W | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
COP | W/W | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 10.15 | 10.15 | 10.15 | 10.15 | 10.16 | 10.15 | 10.15 | 10.15
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Voltage | V | 126.2 | 126.2 | 126.2 | 126.1 | 126.2 | 126.2 | 126.2 | 126.2
Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
60K INDOOR
Capacity | W | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | m³/min | 10.15 | 10.15 | 10.15 | 10.15 | 10.16 | 10.15 | 10.15 | 10.15
Entering DB | ℃ | 20 | 20.01 | 20 | 20.01 | 20 | 20 | 20 | 20
Entering WB | ℃ | 15 | 15.02 | 14.99 | 15.03 | 14.98 | 15 | 15.02 | 14.99
Entering RH | % | 58.93 | 59 | 58.83 | 59.08 | 58.76 | 58.94 | 59.03 | 58.85
Leaving DB | ℃ | 29.81 | 29.8 | 29.8 | 29.81 | 29.8 | 29.81 | 29.8 | 29.82
Leaving WB | ℃ | 29.81 | 29.81 | 29.81 | 29.82 | 29.8 | 29.82 | 29.81 | 29.83
Leaving RH | % | 100.06 | 100.06 | 100.06 | 100.06 | 100.05 | 100.06 | 100.05 | 100.04
Ehthalpy (Ent) | kJ/kg' | 41.887 | 41.925 | 41.844 | 41.954 | 41.816 | 41.887 | 41.927 | 41.856
Enthalpy (Lev) | kJ/kg' | 98.743 | 98.715 | 98.721 | 98.768 | 98.697 | 98.769 | 98.722 | 98.806
Humidity Ratio (Ent) | kg/kg' | 0.008578 | 0.008591 | 0.008562 | 0.008602 | 0.008551 | 0.008578 | 0.008593 | 0.008566
Humidity Ratio (Lev) | kg/kg' | 0.026903 | 0.026895 | 0.026896 | 0.026911 | 0.026889 | 0.026911 | 0.026896 | 0.026922
Specific Heat (Lev) | kJ/kg'-°C | 1.0559 | 1.0558 | 1.0558 | 1.0559 | 1.0558 | 1.0559 | 1.0558 | 1.0559
Specific Volume (Lev) | ㎥/kg | 0.8954 | 0.8953 | 0.8953 | 0.8954 | 0.8953 | 0.8954 | 0.8953 | 0.8954
Static Pressure | mmAq | -0.03 | -0.03 | -0.03 | -0.03 | -0.03 | -0.03 | -0.04 | -0.04
Nozzle Diff. Pressure | mmAq | 28.32 | 28.34 | 28.32 | 28.32 | 28.35 | 28.3 | 28.33 | 28.3
Heat Leakage | W | 85.5 | 85.4 | 85.5 | 85.5 | 85.5 | 85.6 | 85.5 | 85.6
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | W | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 29.81 | 29.8 | 29.8 | 29.81 | 29.8 | 29.81 | 29.8 | 29.82
Nozzle 100/100/125/125 | - | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/-
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY #1 | [6 empty] | LABELO

## 30K ID
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date |  | 5/31/2023 11:21:02 AM
Test Method |  | Heating |  |  | File Name |  | P-20230531 09-07-23.psy
Rated Capacity |  | 0 W |  |  | ID Model Name
Rated Power |  | 2,000 W |  |  | ID Serial Number
Power Source |  | 3P3W / 108 V / 0 Hz |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  | R22 - g |  |  | Exp. Device
ID Entering DB/WB |  | 29 / 19 ℃ |  |  | OD Entering DB/WB |  | 29 / 19 ℃
- |  |  |  |  | -
Note
2kw 10cmm heatloss check
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | W | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
COP | W/W | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 10.15 | 10.15 | 10.15 | 10.15 | 10.16 | 10.15 | 10.15 | 10.15
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W
Voltage | V
Current | A
Frequency | Hz
Power Factor | %
30K INDOOR
Capacity | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | m³/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 17.21 | 19.86 | 20.01 | 20.09 | 20.17 | 20.23 | 15.32 | 4.8
Entering WB | ℃ | 17.29 | 19.94 | 20.09 | 20.18 | 20.26 | 20.31 | 15.38 | 4.86
Entering RH | % | 100.75 | 100.76 | 100.74 | 100.73 | 100.8 | 100.77 | 100.59 | 100.89
Leaving DB | ℃ | 2.36 | 1.46 | 1.45 | 1.44 | 1.44 | 1.43 | 4.17 | 5.1
Leaving WB | ℃ | 2.13 | 1.28 | 1.27 | 1.27 | 1.26 | 1.26 | 3.83 | 4.72
Leaving RH | % | 96.35 | 96.97 | 97.04 | 97.11 | 97.04 | 97.14 | 95.01 | 94.65
Ehthalpy (Ent) | kJ/kg' | 48.682 | 57.207 | 57.717 | 58.012 | 58.29 | 58.486 | 43.066 | 18.319
Enthalpy (Lev) | kJ/kg' | 13.171 | 11.661 | 11.646 | 11.636 | 11.622 | 11.621 | 16.331 | 18.04
Humidity Ratio (Ent) | kg/kg' | 0.012387 | 0.014674 | 0.014814 | 0.014894 | 0.014974 | 0.015027 | 0.010936 | 0.005375
Humidity Ratio (Lev) | kg/kg' | 0.004312 | 0.00407 | 0.004069 | 0.004069 | 0.004065 | 0.004067 | 0.004838 | 0.005145
Specific Heat (Lev) | kJ/kg'-°C | 1.0138 | 1.0134 | 1.0134 | 1.0134 | 1.0134 | 1.0134 | 1.0148 | 1.0154
Specific Volume (Lev) | ㎥/kg | 0.7859 | 0.783 | 0.783 | 0.783 | 0.783 | 0.7829 | 0.7917 | 0.7948
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Heat Leakage | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 2.36 | 1.46 | 1.45 | 1.44 | 1.44 | 1.43 | 4.17 | 5.1
Nozzle 50/60/80/100 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
EER | kcal/hW | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 10.15 | 10.15 | 10.15 | 10.15 | 10.16 | 10.15 | 10.15 | 10.15
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Voltage | V | 126.2 | 126.2 | 126.2 | 126.1 | 126.2 | 126.2 | 126.2 | 126.2
Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
EER | kcal/hW | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 10.15 | 10.15 | 10.15 | 10.15 | 10.16 | 10.15 | 10.15 | 10.15
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Voltage | V | 126.2 | 126.2 | 126.2 | 126.1 | 126.2 | 126.2 | 126.2 | 126.2
Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Voltage | V | 126.2 | 126.2 | 126.2 | 126.1 | 126.2 | 126.2 | 126.2 | 126.2
Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
INDOOR 1
Capacity | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 10.15 | 10.15 | 10.15 | 10.15 | 10.16 | 10.15 | 10.15 | 10.15
Entering DB | ℃ | 20 | 20.01 | 20 | 20.01 | 20 | 20 | 20 | 20
Entering WB | ℃ | 15 | 15.02 | 14.99 | 15.03 | 14.98 | 15 | 15.02 | 14.99
Entering RH | % | 58.93 | 59 | 58.83 | 59.08 | 58.76 | 58.94 | 59.03 | 58.85
Leaving DB | ℃ | 29.81 | 29.8 | 29.8 | 29.81 | 29.8 | 29.81 | 29.8 | 29.82
Leaving WB | ℃ | 29.81 | 29.81 | 29.81 | 29.82 | 29.8 | 29.82 | 29.81 | 29.83
Leaving RH | % | 100.06 | 100.06 | 100.06 | 100.06 | 100.05 | 100.06 | 100.05 | 100.04
Ehthalpy (Ent) | kcal/kg' | 41.887 | 41.925 | 41.844 | 41.954 | 41.816 | 41.887 | 41.927 | 41.856
Enthalpy (Lev) | kcal/kg' | 98.743 | 98.715 | 98.721 | 98.768 | 98.697 | 98.769 | 98.722 | 98.806
Humidity Ratio (Ent) | kg/kg' | 0.008578 | 0.008591 | 0.008562 | 0.008602 | 0.008551 | 0.008578 | 0.008593 | 0.008566
Humidity Ratio (Lev) | kg/kg' | 0.026903 | 0.026895 | 0.026896 | 0.026911 | 0.026889 | 0.026911 | 0.026896 | 0.026922
Specific Heat (Lev) | kcal/kg℃ | 1.0559 | 1.0558 | 1.0558 | 1.0559 | 1.0558 | 1.0559 | 1.0558 | 1.0559
Specific Volume (Lev) | ㎥/kg | 0.8954 | 0.8953 | 0.8953 | 0.8954 | 0.8953 | 0.8954 | 0.8953 | 0.8954
Static Pressure | mmAq | -0.03 | -0.03 | -0.03 | -0.03 | -0.03 | -0.03 | -0.04 | -0.04
Nozzle Diff. Pressure | mmAq | 28.32 | 28.34 | 28.32 | 28.32 | 28.35 | 28.3 | 28.33 | 28.3
Heat Leakage | kcal/h | 85.5 | 85.4 | 85.5 | 85.5 | 85.5 | 85.6 | 85.5 | 85.6
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 29.81 | 29.8 | 29.8 | 29.81 | 29.8 | 29.81 | 29.8 | 29.82
Nozzle 110/140/165/200 | - | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/- | O/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W
Voltage | V
Current | A
Frequency | Hz
Power Factor | %
INDOOR 2
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 17.21 | 19.86 | 20.01 | 20.09 | 20.17 | 20.23 | 15.32 | 4.8
Entering WB | ℃ | 17.29 | 19.94 | 20.09 | 20.18 | 20.26 | 20.31 | 15.38 | 4.86
Entering RH | % | 100.75 | 100.76 | 100.74 | 100.73 | 100.8 | 100.77 | 100.59 | 100.89
Leaving DB | ℃ | 2.36 | 1.46 | 1.45 | 1.44 | 1.44 | 1.43 | 4.17 | 5.1
Leaving WB | ℃ | 2.13 | 1.28 | 1.27 | 1.27 | 1.26 | 1.26 | 3.83 | 4.72
Leaving RH | % | 96.35 | 96.97 | 97.04 | 97.11 | 97.04 | 97.14 | 95.01 | 94.65
Ehthalpy (Ent) | kcal/kg' | 48.682 | 57.207 | 57.717 | 58.012 | 58.29 | 58.486 | 43.066 | 18.319
Enthalpy (Lev) | kcal/kg' | 13.171 | 11.661 | 11.646 | 11.636 | 11.622 | 11.621 | 16.331 | 18.04
Humidity Ratio (Ent) | kg/kg' | 0.012387 | 0.014674 | 0.014814 | 0.014894 | 0.014974 | 0.015027 | 0.010936 | 0.005375
Humidity Ratio (Lev) | kg/kg' | 0.004312 | 0.00407 | 0.004069 | 0.004069 | 0.004065 | 0.004067 | 0.004838 | 0.005145
Specific Heat (Lev) | kcal/kg℃ | 1.0138 | 1.0134 | 1.0134 | 1.0134 | 1.0134 | 1.0134 | 1.0148 | 1.0154
Specific Volume (Lev) | ㎥/kg | 0.7859 | 0.783 | 0.783 | 0.783 | 0.783 | 0.7829 | 0.7917 | 0.7948
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 2.36 | 1.46 | 1.45 | 1.44 | 1.44 | 1.43 | 4.17 | 5.1
Nozzle 60/80/110/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Voltage | V | 126.2 | 126.2 | 126.2 | 126.1 | 126.2 | 126.2 | 126.2 | 126.2
Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Total Capacity | kcal/h | 2041.8 | 2040.3 | 2041.3 | 2041.8 | 2041.6 | 2042.5 | 2041.2 | 2044.1
Total Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Voltage | V | 126.2 | 126.2 | 126.2 | 126.1 | 126.2 | 126.2 | 126.2 | 126.2
Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.011
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Ratio | % | 101.06 | 101.05 | 101.08 | 101.04 | 101.05 | 101.08 | 101.04 | 101.06
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 2021.1 | 2020.9 | 2021.6 | 2020.8 | 2021 | 2021.5 | 2020.9 | 2021.2
Voltage | V | 126.2 | 126.2 | 126.2 | 126.1 | 126.2 | 126.2 | 126.2 | 126.2
Current | A | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24 | 9.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
INDOOR
Entering DB | ℃ | 20 | 20.01 | 20 | 20.01 | 20 | 20 | 20 | 20
Entering WB | ℃ | 15 | 15.02 | 14.99 | 15.03 | 14.98 | 15 | 15.02 | 14.99
Entering RH | % | 58.93 | 59 | 58.83 | 59.08 | 58.76 | 58.94 | 59.03 | 58.85
Barometric Pressure | mmHg | 760 | 760 | 760 | 760 | 760 | 760 | 760 | 760
OUTDOOR
Entering DB | ℃ | 16.89 | 19.6 | 19.65 | 19.7 | 19.75 | 19.8 | 15.1 | 4.63
Entering WB | ℃ | 16.93 | 19.69 | 19.74 | 19.79 | 19.82 | 19.88 | 14.89 | 4.67
Entering RH | % | 100.37 | 100.81 | 100.81 | 100.8 | 100.7 | 100.71 | 97.91 | 100.69
Entering Dew Point | ℃ | 44.17 | 45.65 | 45.21 | 44.67 | 44.15 | 43.66 | 43.09 | 42.72
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.49 | -0.49 | -0.48 | -0.49 | -0.5 | -0.49 | -0.5 | -0.49
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.01 | 0.01
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)