## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | Samsung |  |  | Request No.
Maker |  |  |  |  | Test Date |  | 2023-06-28
Test Method |  | Cooling |  |  | File Name |  | P-20230628 14-47-08.psy
Rated Capacity |  | 18,000 Btu/h |  |  | ID Model Name |  | 4 WAY
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Rodrigo |  |  | OD Serial Number
Refrigerant |  | R32 - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 35 / 24 ℃
- |  |  |  |  | -
Note
Samsung 18k cassete 4 via - Half - 69807
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
EER | Btu/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 15.08 | 15.08 | 15.07 | 15.08 | 15.09 | 15.08 | 15.09
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
60K INDOOR
Capacity | Btu/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Air Flow (Lev) | m³/min | 15.08 | 15.08 | 15.07 | 15.08 | 15.09 | 15.08 | 15.09
Entering DB | ℃ | 27 | 27 | 26.99 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19.03 | 18.95 | 18.95 | 19.02 | 19.04 | 19.04
Entering RH | % | 46.91 | 47.04 | 46.64 | 46.61 | 47 | 47.11 | 47.1
Leaving DB | ℃ | 18.27 | 18.23 | 18.25 | 18.27 | 18.28 | 18.29 | 18.29
Leaving WB | ℃ | 16.11 | 16.12 | 16.05 | 16.05 | 16.12 | 16.15 | 16.14
Leaving RH | % | 80.44 | 80.87 | 80.13 | 79.95 | 80.5 | 80.63 | 80.56
Ehthalpy (Ent) | kJ/kg' | 53.709 | 53.784 | 53.535 | 53.536 | 53.754 | 53.826 | 53.82
Enthalpy (Lev) | kJ/kg' | 45.003 | 45.053 | 44.836 | 44.825 | 45.055 | 45.131 | 45.117
Humidity Ratio (Ent) | kg/kg' | 0.01041 | 0.010439 | 0.010344 | 0.010341 | 0.010428 | 0.010456 | 0.010453
Humidity Ratio (Lev) | kg/kg' | 0.010507 | 0.010541 | 0.010449 | 0.010437 | 0.010522 | 0.010549 | 0.010541
Specific Heat (Lev) | kJ/kg'-°C | 1.0254 | 1.0254 | 1.0253 | 1.0252 | 1.0254 | 1.0254 | 1.0254
Specific Volume (Lev) | ㎥/kg | 0.8368 | 0.8368 | 0.8366 | 0.8365 | 0.8369 | 0.8371 | 0.837
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 26.83 | 26.82 | 26.8 | 26.84 | 26.86 | 26.83 | 26.85
Heat Leakage | Btu/h | 329.1 | 330.5 | 329.8 | 329.3 | 328.6 | 328.3 | 328.2
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | Btu/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | Btu/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 762.43 | 762.39 | 762.54 | 762.64 | 762.45 | 762.24 | 762.34
Nozzle Inlet Temp. | ℃ | 18.27 | 18.23 | 18.25 | 18.27 | 18.28 | 18.29 | 18.29
Nozzle 100/100/125/125 | - | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## 30K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
EER | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 15.08 | 15.08 | 15.07 | 15.08 | 15.09 | 15.08 | 15.09
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
30K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89
Entering DB | ℃ | 21.64 | 21.63 | 21.63 | 21.63 | 21.64 | 21.65 | 21.65
Entering WB | ℃ | 19.19 | 19.22 | 19.16 | 19.16 | 19.2 | 19.19 | 19.22
Entering RH | % | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89
Leaving DB | ℃ | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66
Leaving WB | ℃ | 19.55 | 19.56 | 19.56 | 19.56 | 19.55 | 19.54 | 19.55
Leaving RH | % | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84
Ehthalpy (Ent) | kcal/kg' | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904
Enthalpy (Lev) | kcal/kg' | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059
Humidity Ratio (Ent) | kg/kg' | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486
Humidity Ratio (Lev) | kg/kg' | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043
Specific Heat (Lev) | kcal/kg℃ | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
Specific Volume (Lev) | ㎥/kg | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8
Barometric Pressure | mmHg | 762.43 | 762.39 | 762.54 | 762.64 | 762.45 | 762.24 | 762.34
Nozzle Inlet Temp. | ℃ | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66
Nozzle 50/60/80/100 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
EER | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 15.08 | 15.08 | 15.07 | 15.08 | 15.09 | 15.08 | 15.09
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
EER | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 15.08 | 15.08 | 15.07 | 15.08 | 15.09 | 15.08 | 15.09
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
INDOOR 1
Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Air Flow (Lev) | ㎥/min | 15.08 | 15.08 | 15.07 | 15.08 | 15.09 | 15.08 | 15.09
Entering DB | ℃ | 27 | 27 | 26.99 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19.03 | 18.95 | 18.95 | 19.02 | 19.04 | 19.04
Entering RH | % | 46.91 | 47.04 | 46.64 | 46.61 | 47 | 47.11 | 47.1
Leaving DB | ℃ | 18.27 | 18.23 | 18.25 | 18.27 | 18.28 | 18.29 | 18.29
Leaving WB | ℃ | 16.11 | 16.12 | 16.05 | 16.05 | 16.12 | 16.15 | 16.14
Leaving RH | % | 80.44 | 80.87 | 80.13 | 79.95 | 80.5 | 80.63 | 80.56
Ehthalpy (Ent) | kcal/kg' | 53.709 | 53.784 | 53.535 | 53.536 | 53.754 | 53.826 | 53.82
Enthalpy (Lev) | kcal/kg' | 45.003 | 45.053 | 44.836 | 44.825 | 45.055 | 45.131 | 45.117
Humidity Ratio (Ent) | kg/kg' | 0.01041 | 0.010439 | 0.010344 | 0.010341 | 0.010428 | 0.010456 | 0.010453
Humidity Ratio (Lev) | kg/kg' | 0.010507 | 0.010541 | 0.010449 | 0.010437 | 0.010522 | 0.010549 | 0.010541
Specific Heat (Lev) | kcal/kg℃ | 1.0254 | 1.0254 | 1.0253 | 1.0252 | 1.0254 | 1.0254 | 1.0254
Specific Volume (Lev) | ㎥/kg | 0.8368 | 0.8368 | 0.8366 | 0.8365 | 0.8369 | 0.8371 | 0.837
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 26.83 | 26.82 | 26.8 | 26.84 | 26.86 | 26.83 | 26.85
Heat Leakage | kcal/h | 329.1 | 330.5 | 329.8 | 329.3 | 328.6 | 328.3 | 328.2
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 762.43 | 762.39 | 762.54 | 762.64 | 762.45 | 762.24 | 762.34
Nozzle Inlet Temp. | ℃ | 18.27 | 18.23 | 18.25 | 18.27 | 18.28 | 18.29 | 18.29
Nozzle 110/140/165/200 | - | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
INDOOR 2
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89
Entering DB | ℃ | 21.64 | 21.63 | 21.63 | 21.63 | 21.64 | 21.65 | 21.65
Entering WB | ℃ | 19.19 | 19.22 | 19.16 | 19.16 | 19.2 | 19.19 | 19.22
Entering RH | % | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89
Leaving DB | ℃ | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66
Leaving WB | ℃ | 19.55 | 19.56 | 19.56 | 19.56 | 19.55 | 19.54 | 19.55
Leaving RH | % | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84
Ehthalpy (Ent) | kcal/kg' | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904
Enthalpy (Lev) | kcal/kg' | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059
Humidity Ratio (Ent) | kg/kg' | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486
Humidity Ratio (Lev) | kg/kg' | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043
Specific Heat (Lev) | kcal/kg℃ | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
Specific Volume (Lev) | ㎥/kg | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8
Barometric Pressure | mmHg | 762.43 | 762.39 | 762.54 | 762.64 | 762.45 | 762.24 | 762.34
Nozzle Inlet Temp. | ℃ | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66 | 21.66
Nozzle 60/80/110/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Total Capacity | kcal/h | 9252.9 | 9277.6 | 9242.6 | 9261.2 | 9248.2 | 9238 | 9250
Total Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 18.342 | 18.402 | 18.315 | 18.353 | 18.328 | 18.317 | 18.334
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 51.41 | 51.54 | 51.35 | 51.45 | 51.38 | 51.32 | 51.39
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 504.5 | 504.2 | 504.6 | 504.6 | 504.6 | 504.3 | 504.5
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61 | 2.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.77 | 87.76 | 87.78 | 87.77 | 87.75 | 87.77 | 87.77
INDOOR
Entering DB | ℃ | 27 | 27 | 26.99 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19.03 | 18.95 | 18.95 | 19.02 | 19.04 | 19.04
Entering RH | % | 46.91 | 47.04 | 46.64 | 46.61 | 47 | 47.11 | 47.1
Barometric Pressure | mmHg | 762.43 | 762.39 | 762.54 | 762.64 | 762.45 | 762.24 | 762.34
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.23 | 40.24 | 40.24 | 40.22 | 40.23 | 40.24 | 40.21
Entering Dew Point | ℃ | 19.72 | 19.73 | 19.72 | 19.72 | 19.71 | 19.72 | 19.71
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.66 | -0.66 | -0.66 | -0.65 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-06-28 17:02
Test Time |  | 2:15
Operator |  | Rodrigo
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 13.37%
Relative expanded uncertainty |  | 0.12%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.012 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 805.6 | 2 | 4.63
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 675 | 2 | 3.88
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1016.49 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 42.1 | 2 | 0.02
Indirect contribution | C1 | W | 138.8 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 6.69
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 13.37 (0.12 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)