## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | Samsung |  |  | Request No.
Maker |  |  |  |  | Test Date |  | 2023-06-28
Test Method |  | Cooling |  |  | File Name |  | P-20230628 08-22-52.psy
Rated Capacity |  | 18,000 Btu/h |  |  | ID Model Name |  | 4 WAY
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Rodrigo |  |  | OD Serial Number
Refrigerant |  | R32 - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 29 / 19 ℃
- |  |  |  |  | -
Note
Samsung 18k cassete 4 via - low Half - 69807
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
EER | Btu/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 15.12 | 15.13 | 15.12 | 15.11 | 15.12 | 15.11 | 15.11
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
60K INDOOR
Capacity | Btu/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Air Flow (Lev) | m³/min | 15.12 | 15.13 | 15.12 | 15.11 | 15.12 | 15.11 | 15.11
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19 | 19.02 | 19 | 19 | 19 | 19
Entering RH | % | 46.96 | 46.93 | 47.05 | 46.97 | 46.93 | 46.94 | 46.93
Leaving DB | ℃ | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42
Leaving WB | ℃ | 16.13 | 16.13 | 16.15 | 16.13 | 16.12 | 16.12 | 16.12
Leaving RH | % | 79.42 | 79.37 | 79.59 | 79.47 | 79.38 | 79.36 | 79.36
Ehthalpy (Ent) | kJ/kg' | 53.808 | 53.799 | 53.867 | 53.819 | 53.794 | 53.793 | 53.778
Enthalpy (Lev) | kJ/kg' | 45.153 | 45.152 | 45.211 | 45.164 | 45.137 | 45.132 | 45.124
Humidity Ratio (Ent) | kg/kg' | 0.010449 | 0.010446 | 0.010472 | 0.010454 | 0.010443 | 0.010443 | 0.010438
Humidity Ratio (Lev) | kg/kg' | 0.010504 | 0.010502 | 0.010527 | 0.01051 | 0.010498 | 0.010495 | 0.010492
Specific Heat (Lev) | kJ/kg'-°C | 1.0254 | 1.0254 | 1.0254 | 1.0254 | 1.0253 | 1.0253 | 1.0253
Specific Volume (Lev) | ㎥/kg | 0.8396 | 0.8398 | 0.8398 | 0.8398 | 0.8397 | 0.8395 | 0.8393
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 26.87 | 26.91 | 26.87 | 26.85 | 26.87 | 26.86 | 26.87
Heat Leakage | Btu/h | 323.3 | 323.1 | 323.4 | 323.4 | 323.4 | 323.3 | 323.2
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | Btu/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | Btu/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 760.27 | 760.1 | 760.15 | 760.16 | 760.23 | 760.37 | 760.57
Nozzle Inlet Temp. | ℃ | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42
Nozzle 100/100/125/125 | - | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/-
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY #1 | [6 empty] | LABELO

## 30K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
EER | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 15.12 | 15.13 | 15.12 | 15.11 | 15.12 | 15.11 | 15.11
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
30K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89
Entering DB | ℃ | 21.38 | 21.17 | 21.26 | 21.35 | 21.43 | 21.51 | 21.58
Entering WB | ℃ | 19.99 | 19.61 | 19.83 | 19.98 | 20.09 | 20.18 | 20.25
Entering RH | % | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89
Leaving DB | ℃ | 21.62 | 21.67 | 21.65 | 21.63 | 21.61 | 21.6 | 21.59
Leaving WB | ℃ | 19.43 | 19.43 | 19.42 | 19.42 | 19.43 | 19.44 | 19.45
Leaving RH | % | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84
Ehthalpy (Ent) | kcal/kg' | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904
Enthalpy (Lev) | kcal/kg' | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059
Humidity Ratio (Ent) | kg/kg' | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486
Humidity Ratio (Lev) | kg/kg' | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043
Specific Heat (Lev) | kcal/kg℃ | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
Specific Volume (Lev) | ㎥/kg | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846
Static Pressure | mmAq | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05
Nozzle Diff. Pressure | mmAq | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8
Barometric Pressure | mmHg | 760.27 | 760.1 | 760.15 | 760.16 | 760.23 | 760.37 | 760.57
Nozzle Inlet Temp. | ℃ | 21.62 | 21.67 | 21.65 | 21.63 | 21.61 | 21.6 | 21.59
Nozzle 50/60/80/100 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
EER | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 15.12 | 15.13 | 15.12 | 15.11 | 15.12 | 15.11 | 15.11
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
EER | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 15.12 | 15.13 | 15.12 | 15.11 | 15.12 | 15.11 | 15.11
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
INDOOR 1
Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Air Flow (Lev) | ㎥/min | 15.12 | 15.13 | 15.12 | 15.11 | 15.12 | 15.11 | 15.11
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19 | 19.02 | 19 | 19 | 19 | 19
Entering RH | % | 46.96 | 46.93 | 47.05 | 46.97 | 46.93 | 46.94 | 46.93
Leaving DB | ℃ | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42
Leaving WB | ℃ | 16.13 | 16.13 | 16.15 | 16.13 | 16.12 | 16.12 | 16.12
Leaving RH | % | 79.42 | 79.37 | 79.59 | 79.47 | 79.38 | 79.36 | 79.36
Ehthalpy (Ent) | kcal/kg' | 53.808 | 53.799 | 53.867 | 53.819 | 53.794 | 53.793 | 53.778
Enthalpy (Lev) | kcal/kg' | 45.153 | 45.152 | 45.211 | 45.164 | 45.137 | 45.132 | 45.124
Humidity Ratio (Ent) | kg/kg' | 0.010449 | 0.010446 | 0.010472 | 0.010454 | 0.010443 | 0.010443 | 0.010438
Humidity Ratio (Lev) | kg/kg' | 0.010504 | 0.010502 | 0.010527 | 0.01051 | 0.010498 | 0.010495 | 0.010492
Specific Heat (Lev) | kcal/kg℃ | 1.0254 | 1.0254 | 1.0254 | 1.0254 | 1.0253 | 1.0253 | 1.0253
Specific Volume (Lev) | ㎥/kg | 0.8396 | 0.8398 | 0.8398 | 0.8398 | 0.8397 | 0.8395 | 0.8393
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 26.87 | 26.91 | 26.87 | 26.85 | 26.87 | 26.86 | 26.87
Heat Leakage | kcal/h | 323.3 | 323.1 | 323.4 | 323.4 | 323.4 | 323.3 | 323.2
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 760.27 | 760.1 | 760.15 | 760.16 | 760.23 | 760.37 | 760.57
Nozzle Inlet Temp. | ℃ | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42 | 18.42
Nozzle 110/140/165/200 | - | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
INDOOR 2
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89
Entering DB | ℃ | 21.38 | 21.17 | 21.26 | 21.35 | 21.43 | 21.51 | 21.58
Entering WB | ℃ | 19.99 | 19.61 | 19.83 | 19.98 | 20.09 | 20.18 | 20.25
Entering RH | % | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89
Leaving DB | ℃ | 21.62 | 21.67 | 21.65 | 21.63 | 21.61 | 21.6 | 21.59
Leaving WB | ℃ | 19.43 | 19.43 | 19.42 | 19.42 | 19.43 | 19.44 | 19.45
Leaving RH | % | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84
Ehthalpy (Ent) | kcal/kg' | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904
Enthalpy (Lev) | kcal/kg' | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059
Humidity Ratio (Ent) | kg/kg' | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486
Humidity Ratio (Lev) | kg/kg' | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043
Specific Heat (Lev) | kcal/kg℃ | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
Specific Volume (Lev) | ㎥/kg | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846
Static Pressure | mmAq | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05
Nozzle Diff. Pressure | mmAq | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8
Barometric Pressure | mmHg | 760.27 | 760.1 | 760.15 | 760.16 | 760.23 | 760.37 | 760.57
Nozzle Inlet Temp. | ℃ | 21.62 | 21.67 | 21.65 | 21.63 | 21.61 | 21.6 | 21.59
Nozzle 60/80/110/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Total Capacity | kcal/h | 9185.6 | 9182.9 | 9186.2 | 9181.2 | 9186.8 | 9190.5 | 9186.3
Total Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 23.069 | 23.045 | 23.069 | 23.06 | 23.09 | 23.083 | 23.069
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 51.03 | 51.02 | 51.03 | 51.01 | 51.04 | 51.06 | 51.04
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 398.2 | 398.5 | 398.2 | 398.1 | 397.9 | 398.1 | 398.2
Voltage | V | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3 | 220.3
Current | A | 2.13 | 2.13 | 2.13 | 2.13 | 2.12 | 2.12 | 2.13
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 85.06 | 85.06 | 85.06 | 85.06 | 85.05 | 85.06 | 85.07
INDOOR
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19 | 19.02 | 19 | 19 | 19 | 19
Entering RH | % | 46.96 | 46.93 | 47.05 | 46.97 | 46.93 | 46.94 | 46.93
Barometric Pressure | mmHg | 760.27 | 760.1 | 760.15 | 760.16 | 760.23 | 760.37 | 760.57
OUTDOOR
Entering DB | ℃ | 29.01 | 29.01 | 29 | 29.01 | 29.01 | 29.02 | 29
Entering WB | ℃ | 19 | 19.01 | 19 | 19 | 18.99 | 19 | 18.99
Entering RH | % | 38.45 | 38.5 | 38.47 | 38.45 | 38.4 | 38.45 | 38.42
Entering Dew Point | ℃ | 13.74 | 13.77 | 13.75 | 13.74 | 13.72 | 13.73 | 13.71
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.65 | -0.64 | -0.65 | -0.64 | -0.64 | -0.65 | -0.65
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-06-28 11:20
Test Time |  | 2:57
Operator |  | Rodrigo
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 13.46%
Relative expanded uncertainty |  | 0.13%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.012 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 807.1 | 2 | 4.66
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 677.3 | 2 | 3.91
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1013.61 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 42.1 | 2 | 0.02
Indirect contribution | C1 | W | 137.8 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 6.73
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 13.46 (0.13 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)