## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | Samsung |  |  | Request No.
Maker |  |  |  |  | Test Date |  | 2023-06-28
Test Method |  | Cooling |  |  | File Name |  | P-20230628 11-20-44.psy
Rated Capacity |  | 18,000 Btu/h |  |  | ID Model Name |  | 4 WAY
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Rodrigo |  |  | OD Serial Number
Refrigerant |  | R32 - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 35 / 24 ℃
- |  |  |  |  | -
Note
Samsung 18k cassete 4 via - Standard - 69807
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
EER | Btu/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 14.06 | 14.05 | 14.05 | 14.06 | 14.07 | 14.07 | 14.06
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
60K INDOOR
Capacity | Btu/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Air Flow (Lev) | m³/min | 14.06 | 14.05 | 14.05 | 14.06 | 14.07 | 14.07 | 14.06
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 18.99 | 19.01 | 18.99 | 19.01 | 18.99 | 19
Entering RH | % | 46.91 | 46.85 | 47 | 46.89 | 46.97 | 46.84 | 46.9
Leaving DB | ℃ | 13.1 | 13.1 | 13.11 | 13.1 | 13.1 | 13.09 | 13.08
Leaving WB | ℃ | 12.45 | 12.45 | 12.46 | 12.45 | 12.45 | 12.43 | 12.43
Leaving RH | % | 92.99 | 92.98 | 93.05 | 92.98 | 93 | 92.95 | 92.98
Ehthalpy (Ent) | kJ/kg' | 53.738 | 53.707 | 53.791 | 53.724 | 53.786 | 53.69 | 53.732
Enthalpy (Lev) | kJ/kg' | 35.158 | 35.169 | 35.196 | 35.164 | 35.189 | 35.114 | 35.116
Humidity Ratio (Ent) | kg/kg' | 0.010422 | 0.010409 | 0.010442 | 0.010416 | 0.01044 | 0.010403 | 0.010419
Humidity Ratio (Lev) | kg/kg' | 0.008707 | 0.00871 | 0.008718 | 0.008708 | 0.008716 | 0.008694 | 0.008697
Specific Heat (Lev) | kJ/kg'-°C | 1.022 | 1.022 | 1.022 | 1.022 | 1.022 | 1.022 | 1.022
Specific Volume (Lev) | ㎥/kg | 0.8207 | 0.8208 | 0.8207 | 0.8206 | 0.821 | 0.8203 | 0.8205
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 23.75 | 23.72 | 23.72 | 23.76 | 23.77 | 23.78 | 23.74
Heat Leakage | Btu/h | 524 | 523.8 | 523.7 | 523.8 | 523.8 | 524.4 | 524.6
Drain Weight | kg/h | 1.76 | 1.75 | 1.77 | 1.76 | 1.77 | 1.76 | 1.77
Lantent Heat | Btu/h | 4112 | 4074.1 | 4132.4 | 4098.9 | 4134.3 | 4102.1 | 4130.4
Sensible Heat | Btu/h | 14516.8 | 14502 | 14500 | 14514.5 | 14514.2 | 14538.7 | 14531.3
Sensible Heat Ratio | % | 77.93 | 78.07 | 77.82 | 77.98 | 77.83 | 77.99 | 77.87
Barometric Pressure | mmHg | 761.49 | 761.36 | 761.52 | 761.53 | 761.19 | 761.78 | 761.54
Nozzle Inlet Temp. | ℃ | 13.1 | 13.1 | 13.11 | 13.1 | 13.1 | 13.09 | 13.08
Nozzle 100/100/125/125 | - | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## 30K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
EER | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 14.06 | 14.05 | 14.05 | 14.06 | 14.07 | 14.07 | 14.06
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
30K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89
Entering DB | ℃ | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.61 | 21.61
Entering WB | ℃ | 19.18 | 19.29 | 19.23 | 19.18 | 19.15 | 19.15 | 19.07
Entering RH | % | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89
Leaving DB | ℃ | 21.65 | 21.64 | 21.65 | 21.65 | 21.65 | 21.65 | 21.65
Leaving WB | ℃ | 19.55 | 19.55 | 19.55 | 19.55 | 19.54 | 19.57 | 19.55
Leaving RH | % | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84
Ehthalpy (Ent) | kcal/kg' | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904
Enthalpy (Lev) | kcal/kg' | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059
Humidity Ratio (Ent) | kg/kg' | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486
Humidity Ratio (Lev) | kg/kg' | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043
Specific Heat (Lev) | kcal/kg℃ | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
Specific Volume (Lev) | ㎥/kg | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8
Barometric Pressure | mmHg | 761.49 | 761.36 | 761.52 | 761.53 | 761.19 | 761.78 | 761.54
Nozzle Inlet Temp. | ℃ | 21.65 | 21.64 | 21.65 | 21.65 | 21.65 | 21.65 | 21.65
Nozzle 50/60/80/100 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
EER | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 14.06 | 14.05 | 14.05 | 14.06 | 14.07 | 14.07 | 14.06
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
EER | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 14.06 | 14.05 | 14.05 | 14.06 | 14.07 | 14.07 | 14.06
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
INDOOR 1
Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Air Flow (Lev) | ㎥/min | 14.06 | 14.05 | 14.05 | 14.06 | 14.07 | 14.07 | 14.06
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 18.99 | 19.01 | 18.99 | 19.01 | 18.99 | 19
Entering RH | % | 46.91 | 46.85 | 47 | 46.89 | 46.97 | 46.84 | 46.9
Leaving DB | ℃ | 13.1 | 13.1 | 13.11 | 13.1 | 13.1 | 13.09 | 13.08
Leaving WB | ℃ | 12.45 | 12.45 | 12.46 | 12.45 | 12.45 | 12.43 | 12.43
Leaving RH | % | 92.99 | 92.98 | 93.05 | 92.98 | 93 | 92.95 | 92.98
Ehthalpy (Ent) | kcal/kg' | 53.738 | 53.707 | 53.791 | 53.724 | 53.786 | 53.69 | 53.732
Enthalpy (Lev) | kcal/kg' | 35.158 | 35.169 | 35.196 | 35.164 | 35.189 | 35.114 | 35.116
Humidity Ratio (Ent) | kg/kg' | 0.010422 | 0.010409 | 0.010442 | 0.010416 | 0.01044 | 0.010403 | 0.010419
Humidity Ratio (Lev) | kg/kg' | 0.008707 | 0.00871 | 0.008718 | 0.008708 | 0.008716 | 0.008694 | 0.008697
Specific Heat (Lev) | kcal/kg℃ | 1.022 | 1.022 | 1.022 | 1.022 | 1.022 | 1.022 | 1.022
Specific Volume (Lev) | ㎥/kg | 0.8207 | 0.8208 | 0.8207 | 0.8206 | 0.821 | 0.8203 | 0.8205
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 23.75 | 23.72 | 23.72 | 23.76 | 23.77 | 23.78 | 23.74
Heat Leakage | kcal/h | 524 | 523.8 | 523.7 | 523.8 | 523.8 | 524.4 | 524.6
Drain Weight | kg/h | 1.76 | 1.75 | 1.77 | 1.76 | 1.77 | 1.76 | 1.77
Lantent Heat | kcal/h | 4112 | 4074.1 | 4132.4 | 4098.9 | 4134.3 | 4102.1 | 4130.4
Sensible Heat | kcal/h | 14516.8 | 14502 | 14500 | 14514.5 | 14514.2 | 14538.7 | 14531.3
Sensible Heat Ratio | % | 77.93 | 78.07 | 77.82 | 77.98 | 77.83 | 77.99 | 77.87
Barometric Pressure | mmHg | 761.49 | 761.36 | 761.52 | 761.53 | 761.19 | 761.78 | 761.54
Nozzle Inlet Temp. | ℃ | 13.1 | 13.1 | 13.11 | 13.1 | 13.1 | 13.09 | 13.08
Nozzle 110/140/165/200 | - | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/- | -/-/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
INDOOR 2
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89 | 13.89
Entering DB | ℃ | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.61 | 21.61
Entering WB | ℃ | 19.18 | 19.29 | 19.23 | 19.18 | 19.15 | 19.15 | 19.07
Entering RH | % | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89 | 46.89
Leaving DB | ℃ | 21.65 | 21.64 | 21.65 | 21.65 | 21.65 | 21.65 | 21.65
Leaving WB | ℃ | 19.55 | 19.55 | 19.55 | 19.55 | 19.54 | 19.57 | 19.55
Leaving RH | % | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84 | 70.84
Ehthalpy (Ent) | kcal/kg' | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904 | 53.904
Enthalpy (Lev) | kcal/kg' | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059 | 45.059
Humidity Ratio (Ent) | kg/kg' | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486 | 0.010486
Humidity Ratio (Lev) | kg/kg' | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043 | 0.010043
Specific Heat (Lev) | kcal/kg℃ | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245 | 1.0245
Specific Volume (Lev) | ㎥/kg | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846 | 0.846
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44 | 0.44
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8 | 87.8
Barometric Pressure | mmHg | 761.49 | 761.36 | 761.52 | 761.53 | 761.19 | 761.78 | 761.54
Nozzle Inlet Temp. | ℃ | 21.65 | 21.64 | 21.65 | 21.65 | 21.65 | 21.65 | 21.65
Nozzle 60/80/110/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Total Capacity | kcal/h | 18628.8 | 18576.1 | 18632.4 | 18613.4 | 18648.4 | 18640.8 | 18661.7
Total Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 11.753 | 11.716 | 11.752 | 11.744 | 11.764 | 11.767 | 11.774
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 103.49 | 103.2 | 103.51 | 103.41 | 103.6 | 103.56 | 103.68
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1585.1 | 1585.6 | 1585.4 | 1584.9 | 1585.2 | 1584.2 | 1585
Voltage | V | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2
Current | A | 7.21 | 7.22 | 7.22 | 7.21 | 7.22 | 7.21 | 7.21
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76 | 99.76
INDOOR
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 18.99 | 19.01 | 18.99 | 19.01 | 18.99 | 19
Entering RH | % | 46.91 | 46.85 | 47 | 46.89 | 46.97 | 46.84 | 46.9
Barometric Pressure | mmHg | 761.49 | 761.36 | 761.52 | 761.53 | 761.19 | 761.78 | 761.54
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 35 | 34.99 | 34.99 | 35
Entering WB | ℃ | 23.99 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.25 | 40.22 | 40.27 | 40.24 | 40.25 | 40.26 | 40.24
Entering Dew Point | ℃ | 19.79 | 19.79 | 19.81 | 19.81 | 19.8 | 19.77 | 19.76
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.65 | -0.66 | -0.65 | -0.66 | -0.64 | -0.65 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-06-28 14:47
Test Time |  | 3:26
Operator |  | Rodrigo
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 7.74%
Relative expanded uncertainty |  | 0.04%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.011 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 806.1 | 2 | 2.17
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 527.4 | 2 | 1.42
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1015.24 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 33.2 | 2 | 0.02
Indirect contribution | C1 | W | 279.4 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 3.87
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 7.74 (0.04 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)