## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | Samsung |  |  | Request No.
Maker |  |  |  |  | Test Date |  | 2023-07-03
Test Method |  | Cooling |  |  | File Name |  | P-20230703 11-36-55.psy
Rated Capacity |  | 47,000 Btu/h |  |  | ID Model Name |  | 4 Way
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Rodrigo |  |  | OD Serial Number
Refrigerant |  | R32 - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 29 / 19 ℃
- |  |  |  |  | -
Note
Samsung 47k 4 vias - Low Half - 69814
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
EER | Btu/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 34.53 | 34.54 | 34.52 | 34.52 | 34.53 | 34.52 | 34.53
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
60K INDOOR
Capacity | Btu/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Air Flow (Lev) | m³/min | 34.53 | 34.54 | 34.52 | 34.52 | 34.53 | 34.52 | 34.53
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19.03 | 19 | 19 | 18.99 | 19 | 19
Entering RH | % | 46.95 | 47.1 | 46.95 | 46.91 | 46.9 | 46.93 | 46.92
Leaving DB | ℃ | 17.21 | 17.18 | 17.19 | 17.2 | 17.21 | 17.22 | 17.23
Leaving WB | ℃ | 15.68 | 15.7 | 15.68 | 15.67 | 15.67 | 15.67 | 15.67
Leaving RH | % | 85.61 | 86.07 | 85.71 | 85.57 | 85.46 | 85.45 | 85.38
Ehthalpy (Ent) | kJ/kg' | 53.772 | 53.849 | 53.764 | 53.75 | 53.744 | 53.764 | 53.76
Enthalpy (Lev) | kJ/kg' | 43.837 | 43.908 | 43.829 | 43.812 | 43.81 | 43.834 | 43.829
Humidity Ratio (Ent) | kg/kg' | 0.010435 | 0.010465 | 0.010432 | 0.010427 | 0.010425 | 0.010432 | 0.010431
Humidity Ratio (Lev) | kg/kg' | 0.010475 | 0.010513 | 0.010478 | 0.010468 | 0.010462 | 0.010468 | 0.010464
Specific Heat (Lev) | kJ/kg'-°C | 1.0253 | 1.0254 | 1.0253 | 1.0253 | 1.0253 | 1.0253 | 1.0253
Specific Volume (Lev) | ㎥/kg | 0.8351 | 0.8349 | 0.8349 | 0.8351 | 0.8352 | 0.8353 | 0.8353
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 35.19 | 35.22 | 35.19 | 35.18 | 35.2 | 35.18 | 35.18
Heat Leakage | Btu/h | 369 | 370 | 369.5 | 369.2 | 368.8 | 368.4 | 368.2
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | Btu/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | Btu/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 761.16 | 761.34 | 761.29 | 761.15 | 761.1 | 761.07 | 761.01
Nozzle Inlet Temp. | ℃ | 17.21 | 17.18 | 17.19 | 17.2 | 17.21 | 17.22 | 17.23
Nozzle 100/100/125/125 | - | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY #1 | [6 empty] | LABELO

## 30K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
EER | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 34.53 | 34.54 | 34.52 | 34.52 | 34.53 | 34.52 | 34.53
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
30K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.66 | 21.66 | 21.65 | 21.64 | 21.65 | 21.67 | 21.68
Entering WB | ℃ | 20.01 | 19.77 | 19.88 | 20.02 | 20.13 | 20.13 | 20.12
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 19.92 | 19.74 | 19.82 | 19.89 | 19.96 | 20.03 | 20.09
Leaving WB | ℃ | 18.3 | 18.26 | 18.28 | 18.29 | 18.3 | 18.32 | 18.34
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 761.16 | 761.34 | 761.29 | 761.15 | 761.1 | 761.07 | 761.01
Nozzle Inlet Temp. | ℃ | 19.92 | 19.74 | 19.82 | 19.89 | 19.96 | 20.03 | 20.09
Nozzle 50/60/80/100 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
EER | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 34.53 | 34.54 | 34.52 | 34.52 | 34.53 | 34.52 | 34.53
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
EER | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 34.53 | 34.54 | 34.52 | 34.52 | 34.53 | 34.52 | 34.53
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
INDOOR 1
Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Air Flow (Lev) | ㎥/min | 34.53 | 34.54 | 34.52 | 34.52 | 34.53 | 34.52 | 34.53
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19.03 | 19 | 19 | 18.99 | 19 | 19
Entering RH | % | 46.95 | 47.1 | 46.95 | 46.91 | 46.9 | 46.93 | 46.92
Leaving DB | ℃ | 17.21 | 17.18 | 17.19 | 17.2 | 17.21 | 17.22 | 17.23
Leaving WB | ℃ | 15.68 | 15.7 | 15.68 | 15.67 | 15.67 | 15.67 | 15.67
Leaving RH | % | 85.61 | 86.07 | 85.71 | 85.57 | 85.46 | 85.45 | 85.38
Ehthalpy (Ent) | kcal/kg' | 53.772 | 53.849 | 53.764 | 53.75 | 53.744 | 53.764 | 53.76
Enthalpy (Lev) | kcal/kg' | 43.837 | 43.908 | 43.829 | 43.812 | 43.81 | 43.834 | 43.829
Humidity Ratio (Ent) | kg/kg' | 0.010435 | 0.010465 | 0.010432 | 0.010427 | 0.010425 | 0.010432 | 0.010431
Humidity Ratio (Lev) | kg/kg' | 0.010475 | 0.010513 | 0.010478 | 0.010468 | 0.010462 | 0.010468 | 0.010464
Specific Heat (Lev) | kcal/kg℃ | 1.0253 | 1.0254 | 1.0253 | 1.0253 | 1.0253 | 1.0253 | 1.0253
Specific Volume (Lev) | ㎥/kg | 0.8351 | 0.8349 | 0.8349 | 0.8351 | 0.8352 | 0.8353 | 0.8353
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 35.19 | 35.22 | 35.19 | 35.18 | 35.2 | 35.18 | 35.18
Heat Leakage | kcal/h | 369 | 370 | 369.5 | 369.2 | 368.8 | 368.4 | 368.2
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 761.16 | 761.34 | 761.29 | 761.15 | 761.1 | 761.07 | 761.01
Nozzle Inlet Temp. | ℃ | 17.21 | 17.18 | 17.19 | 17.2 | 17.21 | 17.22 | 17.23
Nozzle 110/140/165/200 | - | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
INDOOR 2
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.66 | 21.66 | 21.65 | 21.64 | 21.65 | 21.67 | 21.68
Entering WB | ℃ | 20.01 | 19.77 | 19.88 | 20.02 | 20.13 | 20.13 | 20.12
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 19.92 | 19.74 | 19.82 | 19.89 | 19.96 | 20.03 | 20.09
Leaving WB | ℃ | 18.3 | 18.26 | 18.28 | 18.29 | 18.3 | 18.32 | 18.34
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 761.16 | 761.34 | 761.29 | 761.15 | 761.1 | 761.07 | 761.01
Nozzle Inlet Temp. | ℃ | 19.92 | 19.74 | 19.82 | 19.89 | 19.96 | 20.03 | 20.09
Nozzle 60/80/110/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Total Capacity | kcal/h | 23731.1 | 23760.2 | 23733.4 | 23736 | 23730.1 | 23711.5 | 23715.1
Total Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 22.342 | 22.346 | 22.315 | 22.352 | 22.338 | 22.357 | 22.342
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 50.49 | 50.55 | 50.5 | 50.5 | 50.49 | 50.45 | 50.46
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1062.2 | 1063.3 | 1063.6 | 1061.9 | 1062.3 | 1060.6 | 1061.5
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.49 | 5.5
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 87.86 | 87.88 | 87.89 | 87.87 | 87.86 | 87.85 | 87.85
INDOOR
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19.03 | 19 | 19 | 18.99 | 19 | 19
Entering RH | % | 46.95 | 47.1 | 46.95 | 46.91 | 46.9 | 46.93 | 46.92
Barometric Pressure | mmHg | 761.16 | 761.34 | 761.29 | 761.15 | 761.1 | 761.07 | 761.01
OUTDOOR
Entering DB | ℃ | 28.99 | 28.98 | 28.99 | 28.99 | 28.98 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.98 | 19 | 18.99 | 18.99 | 18.99 | 18.99
Entering RH | % | 38.48 | 38.46 | 38.5 | 38.49 | 38.51 | 38.47 | 38.48
Entering Dew Point | ℃ | 13.73 | 13.72 | 13.73 | 13.73 | 13.73 | 13.73 | 13.72
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.66 | -0.65 | -0.65 | -0.66 | -0.66 | -0.66 | -0.66
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-07-03 15:29
Test Time |  | 3:52
Operator |  | Rodrigo
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 11.95%
Relative expanded uncertainty |  | 0.04%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.028 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 806.6 | 2 | 4.06
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 657.6 | 2 | 3.31
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1014.8 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 40.9 | 2 | 0.02
Indirect contribution | C1 | W | 356 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 5.97
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 11.95 (0.04 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)