## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | Samsung |  |  | Request No.
Maker |  |  |  |  | Test Date |  | 2023-06-22
Test Method |  | Cooling |  |  | File Name |  | P-20230622 15-59-44.psy
Rated Capacity |  | 53,000 Btu/h |  |  | ID Model Name |  | 4 WAY
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Rodrigo |  |  | OD Serial Number
Refrigerant |  | R32 - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 35 / 24 ℃
- |  |  |  |  | -
Note
Samsung 53k 360 cassete - Standard - 69818
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
EER | Btu/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 29.65 | 29.66 | 29.66 | 29.64 | 29.64 | 29.65 | 29.64
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
60K INDOOR
Capacity | Btu/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Air Flow (Lev) | m³/min | 29.65 | 29.66 | 29.66 | 29.64 | 29.64 | 29.65 | 29.64
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 46.99 | 47 | 46.98 | 46.99 | 46.99 | 46.94 | 47.01
Leaving DB | ℃ | 10.35 | 10.37 | 10.36 | 10.36 | 10.35 | 10.35 | 10.35
Leaving WB | ℃ | 9.82 | 9.83 | 9.82 | 9.83 | 9.82 | 9.82 | 9.82
Leaving RH | % | 93.76 | 93.74 | 93.75 | 93.76 | 93.74 | 93.78 | 93.76
Ehthalpy (Ent) | kJ/kg' | 53.916 | 53.923 | 53.909 | 53.923 | 53.921 | 53.894 | 53.924
Enthalpy (Lev) | kJ/kg' | 28.919 | 28.939 | 28.921 | 28.935 | 28.912 | 28.903 | 28.906
Humidity Ratio (Ent) | kg/kg' | 0.010491 | 0.010494 | 0.010489 | 0.010494 | 0.010494 | 0.010482 | 0.010495
Humidity Ratio (Lev) | kg/kg' | 0.007344 | 0.007347 | 0.007344 | 0.007348 | 0.007342 | 0.007341 | 0.00734
Specific Heat (Lev) | kJ/kg'-°C | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
Specific Volume (Lev) | ㎥/kg | 0.8151 | 0.815 | 0.815 | 0.8152 | 0.8152 | 0.815 | 0.8149
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 26.53 | 26.55 | 26.55 | 26.51 | 26.51 | 26.53 | 26.51
Heat Leakage | Btu/h | 627.4 | 627 | 627.3 | 627.2 | 627.5 | 627.8 | 627.6
Drain Weight | kg/h | 6.87 | 6.87 | 6.87 | 6.86 | 6.88 | 6.86 | 6.88
Lantent Heat | Btu/h | 16029.5 | 16030.3 | 16023.5 | 16016.9 | 16043.8 | 16001.9 | 16060.7
Sensible Heat | Btu/h | 36314.2 | 36308.8 | 36323.2 | 36290 | 36303.1 | 36339.9 | 36320.3
Sensible Heat Ratio | % | 69.38 | 69.37 | 69.39 | 69.38 | 69.35 | 69.43 | 69.34
Barometric Pressure | mmHg | 757.73 | 757.84 | 757.75 | 757.57 | 757.57 | 757.77 | 757.88
Nozzle Inlet Temp. | ℃ | 10.35 | 10.37 | 10.36 | 10.36 | 10.35 | 10.35 | 10.35
Nozzle 100/100/125/125 | - | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## 30K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
EER | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 29.65 | 29.66 | 29.66 | 29.64 | 29.64 | 29.65 | 29.64
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
30K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.53 | 21.49 | 21.51 | 21.53 | 21.55 | 21.55 | 21.54
Entering WB | ℃ | 21.54 | 21.51 | 21.53 | 21.55 | 21.56 | 21.56 | 21.56
Entering RH | % | 100.28 | 100.28 | 100.28 | 100.28 | 100.28 | 100.28 | 100.28
Leaving DB | ℃ | 20.6 | 20.51 | 20.55 | 20.58 | 20.62 | 20.66 | 20.69
Leaving WB | ℃ | 20.58 | 20.49 | 20.53 | 20.56 | 20.6 | 20.64 | 20.67
Leaving RH | % | 100.18 | 100.18 | 100.18 | 100.18 | 100.18 | 100.18 | 100.18
Ehthalpy (Ent) | kcal/kg' | 52.271 | 52.271 | 52.271 | 52.271 | 52.271 | 52.271 | 52.271
Enthalpy (Lev) | kcal/kg' | 54.046 | 54.046 | 54.046 | 54.046 | 54.046 | 54.046 | 54.046
Humidity Ratio (Ent) | kg/kg' | 0.013328 | 0.013328 | 0.013328 | 0.013328 | 0.013328 | 0.013328 | 0.013328
Humidity Ratio (Lev) | kg/kg' | 0.013801 | 0.013801 | 0.013801 | 0.013801 | 0.013801 | 0.013801 | 0.013801
Specific Heat (Lev) | kcal/kg℃ | 1.0315 | 1.0315 | 1.0315 | 1.0315 | 1.0315 | 1.0315 | 1.0315
Specific Volume (Lev) | ㎥/kg | 0.8481 | 0.8481 | 0.8481 | 0.8481 | 0.8481 | 0.8481 | 0.8481
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 757.73 | 757.84 | 757.75 | 757.57 | 757.57 | 757.77 | 757.88
Nozzle Inlet Temp. | ℃ | 20.6 | 20.51 | 20.55 | 20.58 | 20.62 | 20.66 | 20.69
Nozzle 50/60/80/100 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
EER | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 29.65 | 29.66 | 29.66 | 29.64 | 29.64 | 29.65 | 29.64
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
EER | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 29.65 | 29.66 | 29.66 | 29.64 | 29.64 | 29.65 | 29.64
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
INDOOR 1
Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Air Flow (Lev) | ㎥/min | 29.65 | 29.66 | 29.66 | 29.64 | 29.64 | 29.65 | 29.64
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 46.99 | 47 | 46.98 | 46.99 | 46.99 | 46.94 | 47.01
Leaving DB | ℃ | 10.35 | 10.37 | 10.36 | 10.36 | 10.35 | 10.35 | 10.35
Leaving WB | ℃ | 9.82 | 9.83 | 9.82 | 9.83 | 9.82 | 9.82 | 9.82
Leaving RH | % | 93.76 | 93.74 | 93.75 | 93.76 | 93.74 | 93.78 | 93.76
Ehthalpy (Ent) | kcal/kg' | 53.916 | 53.923 | 53.909 | 53.923 | 53.921 | 53.894 | 53.924
Enthalpy (Lev) | kcal/kg' | 28.919 | 28.939 | 28.921 | 28.935 | 28.912 | 28.903 | 28.906
Humidity Ratio (Ent) | kg/kg' | 0.010491 | 0.010494 | 0.010489 | 0.010494 | 0.010494 | 0.010482 | 0.010495
Humidity Ratio (Lev) | kg/kg' | 0.007344 | 0.007347 | 0.007344 | 0.007348 | 0.007342 | 0.007341 | 0.00734
Specific Heat (Lev) | kcal/kg℃ | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195 | 1.0195
Specific Volume (Lev) | ㎥/kg | 0.8151 | 0.815 | 0.815 | 0.8152 | 0.8152 | 0.815 | 0.8149
Static Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Nozzle Diff. Pressure | mmAq | 26.53 | 26.55 | 26.55 | 26.51 | 26.51 | 26.53 | 26.51
Heat Leakage | kcal/h | 627.4 | 627 | 627.3 | 627.2 | 627.5 | 627.8 | 627.6
Drain Weight | kg/h | 6.87 | 6.87 | 6.87 | 6.86 | 6.88 | 6.86 | 6.88
Lantent Heat | kcal/h | 16029.5 | 16030.3 | 16023.5 | 16016.9 | 16043.8 | 16001.9 | 16060.7
Sensible Heat | kcal/h | 36314.2 | 36308.8 | 36323.2 | 36290 | 36303.1 | 36339.9 | 36320.3
Sensible Heat Ratio | % | 69.38 | 69.37 | 69.39 | 69.38 | 69.35 | 69.43 | 69.34
Barometric Pressure | mmHg | 757.73 | 757.84 | 757.75 | 757.57 | 757.57 | 757.77 | 757.88
Nozzle Inlet Temp. | ℃ | 10.35 | 10.37 | 10.36 | 10.36 | 10.35 | 10.35 | 10.35
Nozzle 110/140/165/200 | - | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O | -/-/O/O
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
INDOOR 2
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.53 | 21.49 | 21.51 | 21.53 | 21.55 | 21.55 | 21.54
Entering WB | ℃ | 21.54 | 21.51 | 21.53 | 21.55 | 21.56 | 21.56 | 21.56
Entering RH | % | 100.28 | 100.28 | 100.28 | 100.28 | 100.28 | 100.28 | 100.28
Leaving DB | ℃ | 20.6 | 20.51 | 20.55 | 20.58 | 20.62 | 20.66 | 20.69
Leaving WB | ℃ | 20.58 | 20.49 | 20.53 | 20.56 | 20.6 | 20.64 | 20.67
Leaving RH | % | 100.18 | 100.18 | 100.18 | 100.18 | 100.18 | 100.18 | 100.18
Ehthalpy (Ent) | kcal/kg' | 52.271 | 52.271 | 52.271 | 52.271 | 52.271 | 52.271 | 52.271
Enthalpy (Lev) | kcal/kg' | 54.046 | 54.046 | 54.046 | 54.046 | 54.046 | 54.046 | 54.046
Humidity Ratio (Ent) | kg/kg' | 0.013328 | 0.013328 | 0.013328 | 0.013328 | 0.013328 | 0.013328 | 0.013328
Humidity Ratio (Lev) | kg/kg' | 0.013801 | 0.013801 | 0.013801 | 0.013801 | 0.013801 | 0.013801 | 0.013801
Specific Heat (Lev) | kcal/kg℃ | 1.0315 | 1.0315 | 1.0315 | 1.0315 | 1.0315 | 1.0315 | 1.0315
Specific Volume (Lev) | ㎥/kg | 0.8481 | 0.8481 | 0.8481 | 0.8481 | 0.8481 | 0.8481 | 0.8481
Static Pressure | mmAq | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 757.73 | 757.84 | 757.75 | 757.57 | 757.57 | 757.77 | 757.88
Nozzle Inlet Temp. | ℃ | 20.6 | 20.51 | 20.55 | 20.58 | 20.62 | 20.66 | 20.69
Nozzle 60/80/110/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Total Capacity | kcal/h | 52343.8 | 52339.2 | 52346.7 | 52306.9 | 52346.9 | 52341.8 | 52381
Total Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 9.344 | 9.345 | 9.348 | 9.336 | 9.347 | 9.34 | 9.348
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 98.76 | 98.75 | 98.77 | 98.69 | 98.77 | 98.76 | 98.83
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 5601.9 | 5601 | 5599.8 | 5602.8 | 5600.5 | 5604.3 | 5603.3
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9 | 219.9
Current | A | 25.52 | 25.51 | 25.51 | 25.52 | 25.51 | 25.53 | 25.52
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84 | 99.84
INDOOR
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 27
Entering WB | ℃ | 19 | 19 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 46.99 | 47 | 46.98 | 46.99 | 46.99 | 46.94 | 47.01
Barometric Pressure | mmHg | 757.73 | 757.84 | 757.75 | 757.57 | 757.57 | 757.77 | 757.88
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.98 | 35 | 34.99 | 34.98 | 35
Entering WB | ℃ | 23.99 | 23.99 | 23.99 | 23.99 | 23.99 | 24 | 23.99
Entering RH | % | 40.3 | 40.26 | 40.34 | 40.26 | 40.3 | 40.38 | 40.25
Entering Dew Point | ℃ | 19.7 | 19.7 | 19.71 | 19.69 | 19.7 | 19.72 | 19.69
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.64 | -0.63 | -0.63 | -0.64 | -0.64 | -0.64 | -0.64
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-06-22 18:00
Test Time |  | 2:01
Operator |  | Rodrigo
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 6.82%
Relative expanded uncertainty |  | 0.01%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.024 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 808.7 | 2 | 1.62
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 433.8 | 2 | 0.87
Air dry bulb temperature | T | K | 0.2 | 2 | 0.04
Atmospheric pressure | p | Pa | 1010.22 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 27.9 | 2 | 0.01
Indirect contribution | C1 | W | 785.2 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 3.41
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 6.82 (0.01 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)