## 60K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
EER | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 9.48 | 9.29 | 9.39 | 9.49 | 9.56 | 9.57 | 9.58
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
60K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 19.55 | 19.59 | 19.57 | 19.55 | 19.54 | 19.52 | 19.51
Entering WB | ℃ | 19.52 | 19.56 | 19.54 | 19.52 | 19.49 | 19.49 | 19.5
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 19.96 | 20.04 | 20.01 | 19.98 | 19.94 | 19.91 | 19.88
Leaving WB | ℃ | 16.41 | 16.41 | 16.39 | 16.4 | 16.38 | 16.42 | 16.47
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Nozzle Diff. Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 764.4 | 764.5 | 764.3 | 764.25 | 764 | 764.36 | 764.99
Nozzle Inlet Temp. | ℃ | 19.96 | 20.04 | 20.01 | 19.98 | 19.94 | 19.91 | 19.88
Nozzle 100/100/125/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | Elgin |  |  | Request No.
Maker |  | Elgin |  |  | Test Date |  | 2023-07-28
Test Method |  | Cooling |  |  | File Name |  | P-20230727 22-49-31.psy
Rated Capacity |  | 9,000 Btu/h |  |  | ID Model Name |  | Split Hi-Wall
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Ivan Avila / RSS |  |  | OD Serial Number
Refrigerant |  | R32 - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 35 / 24 ℃
- |  |  |  |  | -
Note
ELGIN - 9K - INVERTER - HALF - 70408
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
EER | Btu/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 9.48 | 9.29 | 9.39 | 9.49 | 9.56 | 9.57 | 9.58
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
30K INDOOR
Capacity | Btu/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Air Flow (Lev) | m³/min | 9.48 | 9.29 | 9.39 | 9.49 | 9.56 | 9.57 | 9.58
Entering DB | ℃ | 27 | 26.99 | 27 | 26.99 | 26.99 | 27 | 27
Entering WB | ℃ | 18.99 | 18.94 | 18.98 | 19.01 | 19.01 | 18.99 | 19
Entering RH | % | 46.79 | 46.55 | 46.71 | 46.96 | 46.93 | 46.76 | 46.84
Leaving DB | ℃ | 19.08 | 18.79 | 18.94 | 19.06 | 19.15 | 19.23 | 19.28
Leaving WB | ℃ | 16.52 | 16.46 | 16.51 | 16.55 | 16.55 | 16.53 | 16.52
Leaving RH | % | 77.51 | 79.31 | 78.46 | 77.9 | 77.15 | 76.32 | 75.96
Ehthalpy (Ent) | kJ/kg' | 53.564 | 53.41 | 53.533 | 53.653 | 53.652 | 53.565 | 53.574
Enthalpy (Lev) | kJ/kg' | 46.128 | 45.961 | 46.092 | 46.236 | 46.232 | 46.141 | 46.109
Humidity Ratio (Ent) | kg/kg' | 0.010354 | 0.010295 | 0.01034 | 0.010391 | 0.01039 | 0.010351 | 0.010358
Humidity Ratio (Lev) | kg/kg' | 0.010624 | 0.010675 | 0.010664 | 0.010672 | 0.010632 | 0.010564 | 0.010534
Specific Heat (Lev) | kJ/kg'-°C | 1.0256 | 1.0257 | 1.0257 | 1.0257 | 1.0256 | 1.0255 | 1.0254
Specific Volume (Lev) | ㎥/kg | 0.8371 | 0.8363 | 0.8369 | 0.8373 | 0.8378 | 0.8376 | 0.837
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 32.98 | 31.7 | 32.37 | 33.01 | 33.5 | 33.61 | 33.67
Heat Leakage | Btu/h | 94.3 | 97.7 | 96 | 94.4 | 93.3 | 92.5 | 91.9
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | Btu/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | Btu/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 764.4 | 764.5 | 764.3 | 764.25 | 764 | 764.36 | 764.99
Nozzle Inlet Temp. | ℃ | 19.08 | 18.79 | 18.94 | 19.06 | 19.15 | 19.23 | 19.28
Nozzle 50/60/80/100 | - | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
EER | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 9.48 | 9.29 | 9.39 | 9.49 | 9.56 | 9.57 | 9.58
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
EER | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 9.48 | 9.29 | 9.39 | 9.49 | 9.56 | 9.57 | 9.58
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
INDOOR 1
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 19.55 | 19.59 | 19.57 | 19.55 | 19.54 | 19.52 | 19.51
Entering WB | ℃ | 19.52 | 19.56 | 19.54 | 19.52 | 19.49 | 19.49 | 19.5
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 19.96 | 20.04 | 20.01 | 19.98 | 19.94 | 19.91 | 19.88
Leaving WB | ℃ | 16.41 | 16.41 | 16.39 | 16.4 | 16.38 | 16.42 | 16.47
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Nozzle Diff. Pressure | mmAq | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 764.4 | 764.5 | 764.3 | 764.25 | 764 | 764.36 | 764.99
Nozzle Inlet Temp. | ℃ | 19.96 | 20.04 | 20.01 | 19.98 | 19.94 | 19.91 | 19.88
Nozzle 110/140/165/200 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
INDOOR 2
Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Air Flow (Lev) | ㎥/min | 9.48 | 9.29 | 9.39 | 9.49 | 9.56 | 9.57 | 9.58
Entering DB | ℃ | 27 | 26.99 | 27 | 26.99 | 26.99 | 27 | 27
Entering WB | ℃ | 18.99 | 18.94 | 18.98 | 19.01 | 19.01 | 18.99 | 19
Entering RH | % | 46.79 | 46.55 | 46.71 | 46.96 | 46.93 | 46.76 | 46.84
Leaving DB | ℃ | 19.08 | 18.79 | 18.94 | 19.06 | 19.15 | 19.23 | 19.28
Leaving WB | ℃ | 16.52 | 16.46 | 16.51 | 16.55 | 16.55 | 16.53 | 16.52
Leaving RH | % | 77.51 | 79.31 | 78.46 | 77.9 | 77.15 | 76.32 | 75.96
Ehthalpy (Ent) | kcal/kg' | 53.564 | 53.41 | 53.533 | 53.653 | 53.652 | 53.565 | 53.574
Enthalpy (Lev) | kcal/kg' | 46.128 | 45.961 | 46.092 | 46.236 | 46.232 | 46.141 | 46.109
Humidity Ratio (Ent) | kg/kg' | 0.010354 | 0.010295 | 0.01034 | 0.010391 | 0.01039 | 0.010351 | 0.010358
Humidity Ratio (Lev) | kg/kg' | 0.010624 | 0.010675 | 0.010664 | 0.010672 | 0.010632 | 0.010564 | 0.010534
Specific Heat (Lev) | kcal/kg℃ | 1.0256 | 1.0257 | 1.0257 | 1.0257 | 1.0256 | 1.0255 | 1.0254
Specific Volume (Lev) | ㎥/kg | 0.8371 | 0.8363 | 0.8369 | 0.8373 | 0.8378 | 0.8376 | 0.837
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 32.98 | 31.7 | 32.37 | 33.01 | 33.5 | 33.61 | 33.67
Heat Leakage | kcal/h | 94.3 | 97.7 | 96 | 94.4 | 93.3 | 92.5 | 91.9
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 764.4 | 764.5 | 764.3 | 764.25 | 764 | 764.36 | 764.99
Nozzle Inlet Temp. | ℃ | 19.08 | 18.79 | 18.94 | 19.06 | 19.15 | 19.23 | 19.28
Nozzle 60/80/110/125 | - | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Total Capacity | kcal/h | 4883.6 | 4803.9 | 4844.5 | 4872.4 | 4908.4 | 4919 | 4951.2
Total Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 12.306 | 12.119 | 12.216 | 12.281 | 12.368 | 12.377 | 12.467
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 54.26 | 53.38 | 53.83 | 54.14 | 54.54 | 54.66 | 55.01
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 396.9 | 396.4 | 396.6 | 396.8 | 396.9 | 397.4 | 397.1
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 3 | 3 | 3 | 3 | 3.01 | 3.01 | 3.01
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 60.02 | 60 | 60 | 60.01 | 60.01 | 60.03 | 60.04
INDOOR
Entering DB | ℃ | 19.55 | 19.59 | 19.57 | 19.55 | 19.54 | 19.52 | 19.51
Entering WB | ℃ | 19.52 | 19.56 | 19.54 | 19.52 | 19.49 | 19.49 | 19.5
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 764.4 | 764.5 | 764.3 | 764.25 | 764 | 764.36 | 764.99
OUTDOOR
Entering DB | ℃ | 34.99 | 34.99 | 34.99 | 34.98 | 34.99 | 35 | 34.99
Entering WB | ℃ | 24 | 24.01 | 23.99 | 23.99 | 23.99 | 23.99 | 24.01
Entering RH | % | 40.23 | 40.29 | 40.2 | 40.22 | 40.2 | 40.19 | 40.29
Entering Dew Point | ℃ | 19.53 | 19.57 | 19.54 | 19.54 | 19.52 | 19.52 | 19.5
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-07-28 00:31
Test Time |  | 1:42
Operator |  | Ivan Avila / RSS
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 15.38%
Relative expanded uncertainty |  | 0.27%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.008 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 803.5 | 2 | 5.4
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 691.9 | 2 | 4.65
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1019.12 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 43.2 | 2 | 0.02
Indirect contribution | C1 | W | 73.3 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 7.69
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 15.38 (0.27 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)