## 60K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
EER | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 9.67 | 9.63 | 9.65 | 9.66 | 9.68 | 9.7 | 9.72
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
60K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 19.78 | 19.67 | 19.71 | 19.75 | 19.8 | 19.85 | 19.91
Entering WB | ℃ | 19.68 | 19.57 | 19.62 | 19.65 | 19.68 | 19.75 | 19.8
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 19.69 | 19.74 | 19.72 | 19.7 | 19.68 | 19.67 | 19.65
Leaving WB | ℃ | 16.52 | 16.46 | 16.48 | 16.5 | 16.54 | 16.55 | 16.58
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Nozzle Diff. Pressure | mmAq | 0.01 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 763.55 | 763.66 | 763.59 | 763.54 | 763.59 | 763.48 | 763.46
Nozzle Inlet Temp. | ℃ | 19.69 | 19.74 | 19.72 | 19.7 | 19.68 | 19.67 | 19.65
Nozzle 100/100/125/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | Elgin |  |  | Request No.
Maker |  | Elgin |  |  | Test Date |  | 2023-07-28
Test Method |  | Cooling |  |  | File Name |  | P-20230728 00-32-26.psy
Rated Capacity |  | 9,000 Btu/h |  |  | ID Model Name |  | Split Hi-Wall
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Bruno Moretti / RSS |  |  | OD Serial Number
Refrigerant |  | R32 - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 29 / 19 ℃
- |  |  |  |  | -
Note
ELGIN - 9K - INVERTER - LOW HALF - 70408
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
EER | Btu/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 9.67 | 9.63 | 9.65 | 9.66 | 9.68 | 9.7 | 9.72
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
30K INDOOR
Capacity | Btu/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Air Flow (Lev) | m³/min | 9.67 | 9.63 | 9.65 | 9.66 | 9.68 | 9.7 | 9.72
Entering DB | ℃ | 27 | 27 | 27 | 26.99 | 27 | 26.99 | 27
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19.01 | 19 | 18.97 | 19.01
Entering RH | % | 46.86 | 46.85 | 46.82 | 46.95 | 46.86 | 46.72 | 46.92
Leaving DB | ℃ | 20.78 | 20.68 | 20.74 | 20.77 | 20.81 | 20.83 | 20.86
Leaving WB | ℃ | 16.97 | 16.95 | 16.96 | 16.99 | 16.98 | 16.96 | 17.01
Leaving RH | % | 68.63 | 69.19 | 68.82 | 68.8 | 68.49 | 68.17 | 68.33
Ehthalpy (Ent) | kJ/kg' | 53.63 | 53.624 | 53.617 | 53.684 | 53.641 | 53.541 | 53.673
Enthalpy (Lev) | kJ/kg' | 47.471 | 47.408 | 47.424 | 47.512 | 47.502 | 47.415 | 47.568
Humidity Ratio (Ent) | kg/kg' | 0.01038 | 0.010378 | 0.010374 | 0.010401 | 0.010383 | 0.010347 | 0.010397
Humidity Ratio (Lev) | kg/kg' | 0.010464 | 0.010481 | 0.010463 | 0.010484 | 0.010463 | 0.010423 | 0.01047
Specific Heat (Lev) | kJ/kg'-°C | 1.0253 | 1.0253 | 1.0253 | 1.0253 | 1.0253 | 1.0252 | 1.0253
Specific Volume (Lev) | ㎥/kg | 0.8427 | 0.8423 | 0.8426 | 0.8428 | 0.8428 | 0.8429 | 0.8431
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 34.11 | 33.82 | 33.96 | 33.99 | 34.17 | 34.29 | 34.4
Heat Leakage | Btu/h | 74 | 75.2 | 74.6 | 74.1 | 73.6 | 73.4 | 73
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | Btu/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | Btu/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 763.55 | 763.66 | 763.59 | 763.54 | 763.59 | 763.48 | 763.46
Nozzle Inlet Temp. | ℃ | 20.78 | 20.68 | 20.74 | 20.77 | 20.81 | 20.83 | 20.86
Nozzle 50/60/80/100 | - | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
EER | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 9.67 | 9.63 | 9.65 | 9.66 | 9.68 | 9.7 | 9.72
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
EER | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 9.67 | 9.63 | 9.65 | 9.66 | 9.68 | 9.7 | 9.72
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
INDOOR 1
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 19.78 | 19.67 | 19.71 | 19.75 | 19.8 | 19.85 | 19.91
Entering WB | ℃ | 19.68 | 19.57 | 19.62 | 19.65 | 19.68 | 19.75 | 19.8
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 19.69 | 19.74 | 19.72 | 19.7 | 19.68 | 19.67 | 19.65
Leaving WB | ℃ | 16.52 | 16.46 | 16.48 | 16.5 | 16.54 | 16.55 | 16.58
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Nozzle Diff. Pressure | mmAq | 0.01 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 763.55 | 763.66 | 763.59 | 763.54 | 763.59 | 763.48 | 763.46
Nozzle Inlet Temp. | ℃ | 19.69 | 19.74 | 19.72 | 19.7 | 19.68 | 19.67 | 19.65
Nozzle 110/140/165/200 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
INDOOR 2
Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Air Flow (Lev) | ㎥/min | 9.67 | 9.63 | 9.65 | 9.66 | 9.68 | 9.7 | 9.72
Entering DB | ℃ | 27 | 27 | 27 | 26.99 | 27 | 26.99 | 27
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19.01 | 19 | 18.97 | 19.01
Entering RH | % | 46.86 | 46.85 | 46.82 | 46.95 | 46.86 | 46.72 | 46.92
Leaving DB | ℃ | 20.78 | 20.68 | 20.74 | 20.77 | 20.81 | 20.83 | 20.86
Leaving WB | ℃ | 16.97 | 16.95 | 16.96 | 16.99 | 16.98 | 16.96 | 17.01
Leaving RH | % | 68.63 | 69.19 | 68.82 | 68.8 | 68.49 | 68.17 | 68.33
Ehthalpy (Ent) | kcal/kg' | 53.63 | 53.624 | 53.617 | 53.684 | 53.641 | 53.541 | 53.673
Enthalpy (Lev) | kcal/kg' | 47.471 | 47.408 | 47.424 | 47.512 | 47.502 | 47.415 | 47.568
Humidity Ratio (Ent) | kg/kg' | 0.01038 | 0.010378 | 0.010374 | 0.010401 | 0.010383 | 0.010347 | 0.010397
Humidity Ratio (Lev) | kg/kg' | 0.010464 | 0.010481 | 0.010463 | 0.010484 | 0.010463 | 0.010423 | 0.01047
Specific Heat (Lev) | kcal/kg℃ | 1.0253 | 1.0253 | 1.0253 | 1.0253 | 1.0253 | 1.0252 | 1.0253
Specific Volume (Lev) | ㎥/kg | 0.8427 | 0.8423 | 0.8426 | 0.8428 | 0.8428 | 0.8429 | 0.8431
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 34.11 | 33.82 | 33.96 | 33.99 | 34.17 | 34.29 | 34.4
Heat Leakage | kcal/h | 74 | 75.2 | 74.6 | 74.1 | 73.6 | 73.4 | 73
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Sensible Heat Ratio | % | 100 | 100 | 100 | 100 | 100 | 100 | 100
Barometric Pressure | mmHg | 763.55 | 763.66 | 763.59 | 763.54 | 763.59 | 763.48 | 763.46
Nozzle Inlet Temp. | ℃ | 20.78 | 20.68 | 20.74 | 20.77 | 20.81 | 20.83 | 20.86
Nozzle 60/80/110/125 | - | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/- | O/-/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Total Capacity | kcal/h | 4094.8 | 4117.8 | 4109.8 | 4096.8 | 4085.5 | 4082.9 | 4075.3
Total Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 17.03 | 17.145 | 17.099 | 17.037 | 16.99 | 16.961 | 16.945
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 45.5 | 45.75 | 45.66 | 45.52 | 45.39 | 45.37 | 45.28
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 240.4 | 240.2 | 240.4 | 240.5 | 240.5 | 240.7 | 240.5
Voltage | V | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1 | 220.1
Current | A | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 57.51 | 57.49 | 57.5 | 57.5 | 57.51 | 57.52 | 57.52
INDOOR
Entering DB | ℃ | 19.78 | 19.67 | 19.71 | 19.75 | 19.8 | 19.85 | 19.91
Entering WB | ℃ | 19.68 | 19.57 | 19.62 | 19.65 | 19.68 | 19.75 | 19.8
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 763.55 | 763.66 | 763.59 | 763.54 | 763.59 | 763.48 | 763.46
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.96 | 19 | 19 | 19 | 18.99 | 19
Entering RH | % | 38.42 | 38.27 | 38.45 | 38.47 | 38.47 | 38.41 | 38.47
Entering Dew Point | ℃ | 13.32 | 13.23 | 13.34 | 13.35 | 13.36 | 13.33 | 13.34
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-07-28 02:15
Test Time |  | 1:42
Operator |  | Bruno Moretti / RSS
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 18.37%
Relative expanded uncertainty |  | 0.39%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.008 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 804.5 | 2 | 6.53
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 712.1 | 2 | 5.78
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1017.98 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 44.5 | 2 | 0.02
Indirect contribution | C1 | W | 61.4 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 9.18
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 18.37 (0.39 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)