## 60K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
EER | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Total Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Air Flow | ㎥/min | 9.8 | 9.77 | 9.78 | 9.78 | 9.79 | 9.82 | 9.83
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
60K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4
Entering WB | ℃ | 18.39 | 18.42 | 18.42 | 18.41 | 18.39 | 18.36 | 18.35
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 21.01 | 20.99 | 21 | 21 | 21.01 | 21.02 | 21.03
Leaving WB | ℃ | 19.89 | 19.87 | 19.88 | 19.88 | 19.89 | 19.89 | 19.9
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760.31 | 760.28 | 760.3 | 760.29 | 760.36 | 760.32 | 760.32
Nozzle Inlet Temp. | ℃ | 21.01 | 20.99 | 21 | 21 | 21.01 | 21.02 | 21.03
Nozzle 100/100/125/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | LG |  |  | Request No.
Maker |  | LG |  |  | Test Date |  | 2023-07-11
Test Method |  | Cooling |  |  | File Name |  | P-20230711 02-21-26.psy
Rated Capacity |  | 12,000 Btu/h |  |  | ID Model Name |  | Split Hi-Wall
Rated Power |  | 1,085 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Bruno Moretti |  |  | OD Serial Number
Refrigerant |  | R410A - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 35 / 24 ℃
- |  |  |  |  | -
Note
LG - 12k - Split - Inverter - half - 70057
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
EER | Btu/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Total Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Air Flow | m³/min | 9.8 | 9.77 | 9.78 | 9.78 | 9.79 | 9.82 | 9.83
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
30K INDOOR
Capacity | Btu/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Air Flow (Lev) | m³/min | 9.8 | 9.77 | 9.78 | 9.78 | 9.79 | 9.82 | 9.83
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 26.99
Entering WB | ℃ | 18.99 | 18.99 | 19 | 19 | 18.99 | 19 | 18.98
Entering RH | % | 46.91 | 46.9 | 46.95 | 46.92 | 46.92 | 46.93 | 46.87
Leaving DB | ℃ | 18.4 | 18.35 | 18.38 | 18.4 | 18.41 | 18.43 | 18.43
Leaving WB | ℃ | 16.06 | 16.05 | 16.07 | 16.06 | 16.06 | 16.07 | 16.06
Leaving RH | % | 79.02 | 79.32 | 79.24 | 79.06 | 78.95 | 78.88 | 78.67
Ehthalpy (Ent) | kJ/kg' | 53.781 | 53.779 | 53.798 | 53.787 | 53.78 | 53.797 | 53.748
Enthalpy (Lev) | kJ/kg' | 44.956 | 44.93 | 44.974 | 44.962 | 44.952 | 44.983 | 44.933
Humidity Ratio (Ent) | kg/kg' | 0.010439 | 0.010437 | 0.010446 | 0.010441 | 0.010438 | 0.010444 | 0.010427
Humidity Ratio (Lev) | kg/kg' | 0.010435 | 0.010443 | 0.01045 | 0.010438 | 0.01043 | 0.010434 | 0.010411
Specific Heat (Lev) | kJ/kg'-°C | 1.0252 | 1.0252 | 1.0253 | 1.0252 | 1.0252 | 1.0252 | 1.0252
Specific Volume (Lev) | ㎥/kg | 0.8394 | 0.8394 | 0.8394 | 0.8395 | 0.8394 | 0.8395 | 0.8395
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 27.82 | 27.67 | 27.73 | 27.75 | 27.81 | 27.94 | 28.02
Heat Leakage | Btu/h | 102.3 | 102.9 | 102.6 | 102.4 | 102.3 | 102 | 101.9
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01
Lantent Heat | Btu/h | 7.1 | 0 | 0 | 3.8 | 13.7 | 16.5 | 25.4
Sensible Heat | Btu/h | 5952.8 | 5960.5 | 5949.5 | 5946.9 | 5947 | 5947.7 | 5947.8
Sensible Heat Ratio | % | 99.88 | 100 | 100 | 99.94 | 99.77 | 99.72 | 99.57
Barometric Pressure | mmHg | 760.31 | 760.28 | 760.3 | 760.29 | 760.36 | 760.32 | 760.32
Nozzle Inlet Temp. | ℃ | 18.4 | 18.35 | 18.38 | 18.4 | 18.41 | 18.43 | 18.43
Nozzle 50/60/80/100 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
EER | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Total Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Air Flow | ㎥/min | 9.8 | 9.77 | 9.78 | 9.78 | 9.79 | 9.82 | 9.83
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
EER | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Total Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Air Flow | ㎥/min | 9.8 | 9.77 | 9.78 | 9.78 | 9.79 | 9.82 | 9.83
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Effective Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
INDOOR 1
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4
Entering WB | ℃ | 18.39 | 18.42 | 18.42 | 18.41 | 18.39 | 18.36 | 18.35
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 21.01 | 20.99 | 21 | 21 | 21.01 | 21.02 | 21.03
Leaving WB | ℃ | 19.89 | 19.87 | 19.88 | 19.88 | 19.89 | 19.89 | 19.9
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760.31 | 760.28 | 760.3 | 760.29 | 760.36 | 760.32 | 760.32
Nozzle Inlet Temp. | ℃ | 21.01 | 20.99 | 21 | 21 | 21.01 | 21.02 | 21.03
Nozzle 110/140/165/200 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Effective Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
INDOOR 2
Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Air Flow (Lev) | ㎥/min | 9.8 | 9.77 | 9.78 | 9.78 | 9.79 | 9.82 | 9.83
Entering DB | ℃ | 27 | 27 | 27 | 27 | 27 | 27 | 26.99
Entering WB | ℃ | 18.99 | 18.99 | 19 | 19 | 18.99 | 19 | 18.98
Entering RH | % | 46.91 | 46.9 | 46.95 | 46.92 | 46.92 | 46.93 | 46.87
Leaving DB | ℃ | 18.4 | 18.35 | 18.38 | 18.4 | 18.41 | 18.43 | 18.43
Leaving WB | ℃ | 16.06 | 16.05 | 16.07 | 16.06 | 16.06 | 16.07 | 16.06
Leaving RH | % | 79.02 | 79.32 | 79.24 | 79.06 | 78.95 | 78.88 | 78.67
Ehthalpy (Ent) | kcal/kg' | 53.781 | 53.779 | 53.798 | 53.787 | 53.78 | 53.797 | 53.748
Enthalpy (Lev) | kcal/kg' | 44.956 | 44.93 | 44.974 | 44.962 | 44.952 | 44.983 | 44.933
Humidity Ratio (Ent) | kg/kg' | 0.010439 | 0.010437 | 0.010446 | 0.010441 | 0.010438 | 0.010444 | 0.010427
Humidity Ratio (Lev) | kg/kg' | 0.010435 | 0.010443 | 0.01045 | 0.010438 | 0.01043 | 0.010434 | 0.010411
Specific Heat (Lev) | kcal/kg℃ | 1.0252 | 1.0252 | 1.0253 | 1.0252 | 1.0252 | 1.0252 | 1.0252
Specific Volume (Lev) | ㎥/kg | 0.8394 | 0.8394 | 0.8394 | 0.8395 | 0.8394 | 0.8395 | 0.8395
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 27.82 | 27.67 | 27.73 | 27.75 | 27.81 | 27.94 | 28.02
Heat Leakage | kcal/h | 102.3 | 102.9 | 102.6 | 102.4 | 102.3 | 102 | 101.9
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01
Lantent Heat | kcal/h | 7.1 | 0 | 0 | 3.8 | 13.7 | 16.5 | 25.4
Sensible Heat | kcal/h | 5952.8 | 5960.5 | 5949.5 | 5946.9 | 5947 | 5947.7 | 5947.8
Sensible Heat Ratio | % | 99.88 | 100 | 100 | 99.94 | 99.77 | 99.72 | 99.57
Barometric Pressure | mmHg | 760.31 | 760.28 | 760.3 | 760.29 | 760.36 | 760.32 | 760.32
Nozzle Inlet Temp. | ℃ | 18.4 | 18.35 | 18.38 | 18.4 | 18.41 | 18.43 | 18.43
Nozzle 60/80/110/125 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Effective Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Total Capacity | kcal/h | 5959.8 | 5960.5 | 5949.5 | 5950.7 | 5960.7 | 5964.2 | 5973.2
Total Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Effective Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
EER Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 13.874 | 13.872 | 13.849 | 13.852 | 13.874 | 13.888 | 13.907
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 49.67 | 49.67 | 49.58 | 49.59 | 49.67 | 49.7 | 49.78
Effective Power Ratio | % | 39.59 | 39.6 | 39.59 | 39.59 | 39.6 | 39.58 | 39.59
COPc Ratio | % | 125.44 | 125.43 | 125.22 | 125.25 | 125.44 | 125.57 | 125.74
Total Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Total Current Ratio | % | 39.67 | 39.67 | 39.66 | 39.67 | 39.67 | 39.66 | 39.67
Power Input | W | 429.6 | 429.7 | 429.6 | 429.6 | 429.6 | 429.4 | 429.5
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.05 | 82.06
INDOOR
Entering DB | ℃ | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4 | 21.4
Entering WB | ℃ | 18.39 | 18.42 | 18.42 | 18.41 | 18.39 | 18.36 | 18.35
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760.31 | 760.28 | 760.3 | 760.29 | 760.36 | 760.32 | 760.32
OUTDOOR
Entering DB | ℃ | 34.99 | 35 | 34.99 | 35 | 34.99 | 34.99 | 34.99
Entering WB | ℃ | 23.99 | 24 | 23.98 | 23.99 | 23.99 | 23.99 | 23.99
Entering RH | % | 40.26 | 40.29 | 40.25 | 40.27 | 40.26 | 40.28 | 40.24
Entering Dew Point | ℃ | 19.74 | 19.76 | 19.74 | 19.75 | 19.74 | 19.75 | 19.74
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68 | -0.68
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-07-11 04:22
Test Time |  | 2:01
Operator |  | Bruno Moretti
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 13.23%
Relative expanded uncertainty |  | 0.19%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.008 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 806.7 | 2 | 4.57
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 674.3 | 2 | 3.82
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1013.66 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 42 | 2 | 0.02
Indirect contribution | C1 | W | 89.4 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 6.62
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 13.23 (0.19 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)