## 60K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
EER | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Total Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Air Flow | ㎥/min | 9.89 | 9.86 | 9.87 | 9.89 | 9.89 | 9.9 | 9.9
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
60K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.45 | 21.44 | 21.45 | 21.45 | 21.45 | 21.45 | 21.45
Entering WB | ℃ | 18.36 | 18.32 | 18.34 | 18.35 | 18.38 | 18.38 | 18.38
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 21.1 | 21.09 | 21.09 | 21.1 | 21.11 | 21.11 | 21.12
Leaving WB | ℃ | 19.96 | 19.95 | 19.96 | 19.96 | 19.98 | 19.98 | 19.97
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760.32 | 760.26 | 760.29 | 760.21 | 760.48 | 760.41 | 760.29
Nozzle Inlet Temp. | ℃ | 21.1 | 21.09 | 21.09 | 21.1 | 21.11 | 21.11 | 21.12
Nozzle 100/100/125/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY #1 | [6 empty] | LABELO

## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | LG |  |  | Request No.
Maker |  | LG |  |  | Test Date |  | 2023-07-11
Test Method |  | Cooling |  |  | File Name |  | P-20230711 04-29-11.psy
Rated Capacity |  | 12,000 Btu/h |  |  | ID Model Name |  | Split Hi-Wall
Rated Power |  | 1,085 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Bruno Moretti |  |  | OD Serial Number
Refrigerant |  | R410A - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 29 / 19 ℃
- |  |  |  |  | -
Note
LG - 12k - Split - Inverter - Low Half - 70057
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
EER | Btu/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Total Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Air Flow | m³/min | 9.89 | 9.86 | 9.87 | 9.89 | 9.89 | 9.9 | 9.9
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
30K INDOOR
Capacity | Btu/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Air Flow (Lev) | m³/min | 9.89 | 9.86 | 9.87 | 9.89 | 9.89 | 9.9 | 9.9
Entering DB | ℃ | 26.99 | 26.99 | 27 | 26.99 | 27 | 26.99 | 26.99
Entering WB | ℃ | 18.99 | 19 | 18.99 | 19.01 | 18.98 | 19 | 18.99
Entering RH | % | 46.92 | 46.98 | 46.89 | 46.99 | 46.85 | 46.95 | 46.88
Leaving DB | ℃ | 19.05 | 19 | 19.03 | 19.04 | 19.07 | 19.09 | 19.09
Leaving WB | ℃ | 16.3 | 16.3 | 16.29 | 16.31 | 16.29 | 16.31 | 16.29
Leaving RH | % | 75.85 | 76.26 | 75.99 | 76.02 | 75.64 | 75.63 | 75.53
Ehthalpy (Ent) | kJ/kg' | 53.78 | 53.808 | 53.765 | 53.822 | 53.735 | 53.791 | 53.758
Enthalpy (Lev) | kJ/kg' | 45.625 | 45.633 | 45.606 | 45.663 | 45.585 | 45.655 | 45.608
Humidity Ratio (Ent) | kg/kg' | 0.010439 | 0.010451 | 0.010433 | 0.010456 | 0.010421 | 0.010444 | 0.010431
Humidity Ratio (Lev) | kg/kg' | 0.010434 | 0.010458 | 0.010437 | 0.010453 | 0.010413 | 0.01043 | 0.010413
Specific Heat (Lev) | kJ/kg'-°C | 1.0252 | 1.0253 | 1.0252 | 1.0253 | 1.0252 | 1.0252 | 1.0252
Specific Volume (Lev) | ㎥/kg | 0.8413 | 0.8413 | 0.8413 | 0.8414 | 0.8412 | 0.8413 | 0.8414
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 28.27 | 28.13 | 28.2 | 28.29 | 28.33 | 28.33 | 28.35
Heat Leakage | Btu/h | 94.5 | 95.1 | 94.8 | 94.7 | 94.4 | 94 | 94.1
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01
Lantent Heat | Btu/h | 8.8 | 0 | 0 | 4.4 | 13.9 | 23.1 | 29.1
Sensible Heat | Btu/h | 5535.6 | 5545.1 | 5541.4 | 5543.9 | 5532.5 | 5513.7 | 5519.2
Sensible Heat Ratio | % | 99.84 | 100 | 100 | 99.92 | 99.75 | 99.58 | 99.48
Barometric Pressure | mmHg | 760.32 | 760.26 | 760.29 | 760.21 | 760.48 | 760.41 | 760.29
Nozzle Inlet Temp. | ℃ | 19.05 | 19 | 19.03 | 19.04 | 19.07 | 19.09 | 19.09
Nozzle 50/60/80/100 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
EER | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Total Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Air Flow | ㎥/min | 9.89 | 9.86 | 9.87 | 9.89 | 9.89 | 9.9 | 9.9
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
EER | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Total Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Air Flow | ㎥/min | 9.89 | 9.86 | 9.87 | 9.89 | 9.89 | 9.9 | 9.9
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Effective Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
INDOOR 1
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 21.45 | 21.44 | 21.45 | 21.45 | 21.45 | 21.45 | 21.45
Entering WB | ℃ | 18.36 | 18.32 | 18.34 | 18.35 | 18.38 | 18.38 | 18.38
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 21.1 | 21.09 | 21.09 | 21.1 | 21.11 | 21.11 | 21.12
Leaving WB | ℃ | 19.96 | 19.95 | 19.96 | 19.96 | 19.98 | 19.98 | 19.97
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760.32 | 760.26 | 760.29 | 760.21 | 760.48 | 760.41 | 760.29
Nozzle Inlet Temp. | ℃ | 21.1 | 21.09 | 21.09 | 21.1 | 21.11 | 21.11 | 21.12
Nozzle 110/140/165/200 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Effective Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
INDOOR 2
Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Air Flow (Lev) | ㎥/min | 9.89 | 9.86 | 9.87 | 9.89 | 9.89 | 9.9 | 9.9
Entering DB | ℃ | 26.99 | 26.99 | 27 | 26.99 | 27 | 26.99 | 26.99
Entering WB | ℃ | 18.99 | 19 | 18.99 | 19.01 | 18.98 | 19 | 18.99
Entering RH | % | 46.92 | 46.98 | 46.89 | 46.99 | 46.85 | 46.95 | 46.88
Leaving DB | ℃ | 19.05 | 19 | 19.03 | 19.04 | 19.07 | 19.09 | 19.09
Leaving WB | ℃ | 16.3 | 16.3 | 16.29 | 16.31 | 16.29 | 16.31 | 16.29
Leaving RH | % | 75.85 | 76.26 | 75.99 | 76.02 | 75.64 | 75.63 | 75.53
Ehthalpy (Ent) | kcal/kg' | 53.78 | 53.808 | 53.765 | 53.822 | 53.735 | 53.791 | 53.758
Enthalpy (Lev) | kcal/kg' | 45.625 | 45.633 | 45.606 | 45.663 | 45.585 | 45.655 | 45.608
Humidity Ratio (Ent) | kg/kg' | 0.010439 | 0.010451 | 0.010433 | 0.010456 | 0.010421 | 0.010444 | 0.010431
Humidity Ratio (Lev) | kg/kg' | 0.010434 | 0.010458 | 0.010437 | 0.010453 | 0.010413 | 0.01043 | 0.010413
Specific Heat (Lev) | kcal/kg℃ | 1.0252 | 1.0253 | 1.0252 | 1.0253 | 1.0252 | 1.0252 | 1.0252
Specific Volume (Lev) | ㎥/kg | 0.8413 | 0.8413 | 0.8413 | 0.8414 | 0.8412 | 0.8413 | 0.8414
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 28.27 | 28.13 | 28.2 | 28.29 | 28.33 | 28.33 | 28.35
Heat Leakage | kcal/h | 94.5 | 95.1 | 94.8 | 94.7 | 94.4 | 94 | 94.1
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01
Lantent Heat | kcal/h | 8.8 | 0 | 0 | 4.4 | 13.9 | 23.1 | 29.1
Sensible Heat | kcal/h | 5535.6 | 5545.1 | 5541.4 | 5543.9 | 5532.5 | 5513.7 | 5519.2
Sensible Heat Ratio | % | 99.84 | 100 | 100 | 99.92 | 99.75 | 99.58 | 99.48
Barometric Pressure | mmHg | 760.32 | 760.26 | 760.29 | 760.21 | 760.48 | 760.41 | 760.29
Nozzle Inlet Temp. | ℃ | 19.05 | 19 | 19.03 | 19.04 | 19.07 | 19.09 | 19.09
Nozzle 60/80/110/125 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Effective Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Total Capacity | kcal/h | 5544.4 | 5545.1 | 5541.4 | 5548.2 | 5546.4 | 5536.8 | 5548.3
Total Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Effective Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
EER Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 18.96 | 18.954 | 18.953 | 18.958 | 18.976 | 18.967 | 18.953
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 46.2 | 46.21 | 46.18 | 46.24 | 46.22 | 46.14 | 46.24
Effective Power Ratio | % | 26.95 | 26.96 | 26.95 | 26.97 | 26.94 | 26.9 | 26.98
COPc Ratio | % | 171.43 | 171.38 | 171.37 | 171.41 | 171.57 | 171.49 | 171.37
Total Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Total Current Ratio | % | 26.73 | 26.75 | 26.73 | 26.76 | 26.71 | 26.68 | 26.76
Power Input | W | 292.4 | 292.6 | 292.4 | 292.7 | 292.3 | 291.9 | 292.7
Voltage | V | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | A | 1.6 | 1.6 | 1.6 | 1.61 | 1.6 | 1.6 | 1.61
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 82.88 | 82.88 | 82.88 | 82.88 | 82.89 | 82.9 | 82.88
INDOOR
Entering DB | ℃ | 21.45 | 21.44 | 21.45 | 21.45 | 21.45 | 21.45 | 21.45
Entering WB | ℃ | 18.36 | 18.32 | 18.34 | 18.35 | 18.38 | 18.38 | 18.38
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 760.32 | 760.26 | 760.29 | 760.21 | 760.48 | 760.41 | 760.29
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 18.98 | 19 | 19 | 18.99
Entering RH | % | 38.5 | 38.51 | 38.49 | 38.45 | 38.53 | 38.53 | 38.5
Entering Dew Point | ℃ | 13.69 | 13.69 | 13.69 | 13.68 | 13.7 | 13.7 | 13.69
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -0.67 | -0.67 | -0.67 | -0.67 | -0.66 | -0.67 | -0.67
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-07-11 06:59
Test Time |  | 2:30
Operator |  | Bruno Moretti
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 14.19%
Relative expanded uncertainty |  | 0.22%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.008 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 806.7 | 2 | 4.95
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 684.4 | 2 | 4.2
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1013.68 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 42.6 | 2 | 0.02
Indirect contribution | C1 | W | 83.2 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 7.1
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 14.19 (0.22 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)