## 60K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
EER | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 12.71 | 12.72 | 12.71 | 12.71 | 12.71 | 12.71 | 12.7
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
60K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
Entering DB | ℃ | 20.52 | 20.51 | 20.51 | 20.52 | 20.52 | 20.52 | 20.54
Entering WB | ℃ | 17.21 | 17.43 | 17.32 | 17.23 | 17.16 | 17.1 | 17.02
Entering RH | % | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71
Leaving DB | ℃ | 20.58 | 20.59 | 20.59 | 20.58 | 20.58 | 20.57 | 20.56
Leaving WB | ℃ | 19.75 | 19.76 | 19.76 | 19.75 | 19.74 | 19.74 | 19.74
Leaving RH | % | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1
Ehthalpy (Ent) | kcal/kg' | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48
Enthalpy (Lev) | kcal/kg' | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145
Humidity Ratio (Ent) | kg/kg' | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324
Humidity Ratio (Lev) | kg/kg' | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083
Specific Heat (Lev) | kcal/kg℃ | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246
Specific Volume (Lev) | ㎥/kg | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256
Static Pressure | mmAq | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27
Barometric Pressure | mmHg | 767.89 | 767.88 | 767.93 | 767.96 | 767.91 | 767.87 | 767.81
Nozzle Inlet Temp. | ℃ | 20.58 | 20.59 | 20.59 | 20.58 | 20.58 | 20.57 | 20.56
Nozzle 100/100/125/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | TCL |  |  | Request No.
Maker |  | TCL |  |  | Test Date |  | 2023-08-08
Test Method |  | Cooling |  |  | File Name |  | P-20230808 00-08-04.psy
Rated Capacity |  | 18,000 Btu/h |  |  | ID Model Name
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Bruno Moretti / RSS |  |  | OD Serial Number
Refrigerant |  | R410A - g |  |  | Exp. Device
ID Entering DB/WB |  | 26.7 / 19.4 ℃ |  |  | OD Entering DB/WB |  | 35 / 23.9 ℃
- |  |  |  |  | -
Note
TCL - 18k - Split - Fixa- Standard - 69983
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
EER | Btu/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 12.71 | 12.72 | 12.71 | 12.71 | 12.71 | 12.71 | 12.7
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
30K INDOOR
Capacity | Btu/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Air Flow (Lev) | m³/min | 12.71 | 12.72 | 12.71 | 12.71 | 12.71 | 12.71 | 12.7
Entering DB | ℃ | 26.7 | 26.69 | 26.7 | 26.7 | 26.7 | 26.7 | 26.69
Entering WB | ℃ | 19.39 | 19.38 | 19.33 | 19.4 | 19.41 | 19.41 | 19.39
Entering RH | % | 50.45 | 50.45 | 50.11 | 50.51 | 50.56 | 50.57 | 50.49
Leaving DB | ℃ | 13.91 | 13.92 | 13.87 | 13.91 | 13.92 | 13.93 | 13.91
Leaving WB | ℃ | 13.03 | 13.04 | 12.97 | 13.03 | 13.04 | 13.04 | 13.03
Leaving RH | % | 90.71 | 90.75 | 90.62 | 90.76 | 90.74 | 90.73 | 90.68
Ehthalpy (Ent) | kJ/kg' | 54.722 | 54.716 | 54.53 | 54.755 | 54.79 | 54.796 | 54.743
Enthalpy (Lev) | kJ/kg' | 36.436 | 36.476 | 36.299 | 36.45 | 36.471 | 36.482 | 36.44
Humidity Ratio (Ent) | kg/kg' | 0.010928 | 0.010928 | 0.010854 | 0.010941 | 0.010954 | 0.010957 | 0.010938
Humidity Ratio (Lev) | kg/kg' | 0.008884 | 0.008895 | 0.008848 | 0.008889 | 0.008893 | 0.008895 | 0.008884
Specific Heat (Lev) | kJ/kg'-°C | 1.0223 | 1.0224 | 1.0223 | 1.0224 | 1.0224 | 1.0224 | 1.0223
Specific Volume (Lev) | ㎥/kg | 0.8163 | 0.8164 | 0.8161 | 0.8163 | 0.8164 | 0.8164 | 0.8164
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 47.92 | 48.01 | 47.94 | 47.95 | 47.91 | 47.89 | 47.84
Heat Leakage | Btu/h | 152.2 | 152 | 152.7 | 152.2 | 152.1 | 152 | 152.1
Drain Weight | kg/h | 1.91 | 1.9 | 1.87 | 1.92 | 1.93 | 1.93 | 1.92
Lantent Heat | Btu/h | 4456 | 4434.3 | 4372.6 | 4473.8 | 4491.6 | 4491.7 | 4472
Sensible Heat | Btu/h | 11888.4 | 11884.1 | 11929.9 | 11893.3 | 11879.2 | 11871.4 | 11872.4
Sensible Heat Ratio | % | 72.74 | 72.83 | 73.18 | 72.67 | 72.56 | 72.55 | 72.64
Barometric Pressure | mmHg | 767.89 | 767.88 | 767.93 | 767.96 | 767.91 | 767.87 | 767.81
Nozzle Inlet Temp. | ℃ | 13.91 | 13.92 | 13.87 | 13.91 | 13.92 | 13.93 | 13.91
Nozzle 50/60/80/100 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
EER | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 12.71 | 12.72 | 12.71 | 12.71 | 12.71 | 12.71 | 12.7
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
EER | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 12.71 | 12.72 | 12.71 | 12.71 | 12.71 | 12.71 | 12.7
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
INDOOR 1
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
Entering DB | ℃ | 20.52 | 20.51 | 20.51 | 20.52 | 20.52 | 20.52 | 20.54
Entering WB | ℃ | 17.21 | 17.43 | 17.32 | 17.23 | 17.16 | 17.1 | 17.02
Entering RH | % | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71
Leaving DB | ℃ | 20.58 | 20.59 | 20.59 | 20.58 | 20.58 | 20.57 | 20.56
Leaving WB | ℃ | 19.75 | 19.76 | 19.76 | 19.75 | 19.74 | 19.74 | 19.74
Leaving RH | % | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1
Ehthalpy (Ent) | kcal/kg' | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48
Enthalpy (Lev) | kcal/kg' | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145
Humidity Ratio (Ent) | kg/kg' | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324
Humidity Ratio (Lev) | kg/kg' | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083
Specific Heat (Lev) | kcal/kg℃ | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246
Specific Volume (Lev) | ㎥/kg | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256
Static Pressure | mmAq | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27
Barometric Pressure | mmHg | 767.89 | 767.88 | 767.93 | 767.96 | 767.91 | 767.87 | 767.81
Nozzle Inlet Temp. | ℃ | 20.58 | 20.59 | 20.59 | 20.58 | 20.58 | 20.57 | 20.56
Nozzle 110/140/165/200 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
INDOOR 2
Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Air Flow (Lev) | ㎥/min | 12.71 | 12.72 | 12.71 | 12.71 | 12.71 | 12.71 | 12.7
Entering DB | ℃ | 26.7 | 26.69 | 26.7 | 26.7 | 26.7 | 26.7 | 26.69
Entering WB | ℃ | 19.39 | 19.38 | 19.33 | 19.4 | 19.41 | 19.41 | 19.39
Entering RH | % | 50.45 | 50.45 | 50.11 | 50.51 | 50.56 | 50.57 | 50.49
Leaving DB | ℃ | 13.91 | 13.92 | 13.87 | 13.91 | 13.92 | 13.93 | 13.91
Leaving WB | ℃ | 13.03 | 13.04 | 12.97 | 13.03 | 13.04 | 13.04 | 13.03
Leaving RH | % | 90.71 | 90.75 | 90.62 | 90.76 | 90.74 | 90.73 | 90.68
Ehthalpy (Ent) | kcal/kg' | 54.722 | 54.716 | 54.53 | 54.755 | 54.79 | 54.796 | 54.743
Enthalpy (Lev) | kcal/kg' | 36.436 | 36.476 | 36.299 | 36.45 | 36.471 | 36.482 | 36.44
Humidity Ratio (Ent) | kg/kg' | 0.010928 | 0.010928 | 0.010854 | 0.010941 | 0.010954 | 0.010957 | 0.010938
Humidity Ratio (Lev) | kg/kg' | 0.008884 | 0.008895 | 0.008848 | 0.008889 | 0.008893 | 0.008895 | 0.008884
Specific Heat (Lev) | kcal/kg℃ | 1.0223 | 1.0224 | 1.0223 | 1.0224 | 1.0224 | 1.0224 | 1.0223
Specific Volume (Lev) | ㎥/kg | 0.8163 | 0.8164 | 0.8161 | 0.8163 | 0.8164 | 0.8164 | 0.8164
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 47.92 | 48.01 | 47.94 | 47.95 | 47.91 | 47.89 | 47.84
Heat Leakage | kcal/h | 152.2 | 152 | 152.7 | 152.2 | 152.1 | 152 | 152.1
Drain Weight | kg/h | 1.91 | 1.9 | 1.87 | 1.92 | 1.93 | 1.93 | 1.92
Lantent Heat | kcal/h | 4456 | 4434.3 | 4372.6 | 4473.8 | 4491.6 | 4491.7 | 4472
Sensible Heat | kcal/h | 11888.4 | 11884.1 | 11929.9 | 11893.3 | 11879.2 | 11871.4 | 11872.4
Sensible Heat Ratio | % | 72.74 | 72.83 | 73.18 | 72.67 | 72.56 | 72.55 | 72.64
Barometric Pressure | mmHg | 767.89 | 767.88 | 767.93 | 767.96 | 767.91 | 767.87 | 767.81
Nozzle Inlet Temp. | ℃ | 13.91 | 13.92 | 13.87 | 13.91 | 13.92 | 13.93 | 13.91
Nozzle 60/80/110/125 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Total Capacity | kcal/h | 16344.4 | 16318.4 | 16302.5 | 16367.1 | 16370.8 | 16363.1 | 16344.4
Total Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 11.149 | 11.122 | 11.121 | 11.161 | 11.168 | 11.164 | 11.16
Power Input | W | 1466 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 90.8 | 90.66 | 90.57 | 90.93 | 90.95 | 90.91 | 90.8
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1465.9 | 1467.2 | 1465.9 | 1466.5 | 1465.9 | 1465.6 | 1464.6
Voltage | V | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8 | 219.8
Current | A | 6.82 | 6.83 | 6.82 | 6.83 | 6.82 | 6.82 | 6.82
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 97.72 | 97.73 | 97.72 | 97.72 | 97.72 | 97.72 | 97.71
INDOOR
Entering DB | ℃ | 20.52 | 20.51 | 20.51 | 20.52 | 20.52 | 20.52 | 20.54
Entering WB | ℃ | 17.21 | 17.43 | 17.32 | 17.23 | 17.16 | 17.1 | 17.02
Entering RH | % | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71
Barometric Pressure | mmHg | 767.89 | 767.88 | 767.93 | 767.96 | 767.91 | 767.87 | 767.81
OUTDOOR
Entering DB | ℃ | 35 | 35 | 35 | 35 | 35 | 35 | 34.99
Entering WB | ℃ | 23.89 | 23.89 | 23.9 | 23.9 | 23.89 | 23.9 | 23.89
Entering RH | % | 39.7 | 39.67 | 39.72 | 39.7 | 39.69 | 39.72 | 39.7
Entering Dew Point | ℃ | 19.37 | 19.37 | 19.38 | 19.37 | 19.35 | 19.36 | 19.36
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-08-08 02:21
Test Time |  | 2:13
Operator |  | Bruno Moretti / RSS
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 7.88%
Relative expanded uncertainty |  | 0.04%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.01 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 820.8 | 2 | 2.24
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 546.5 | 2 | 1.49
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1023.77 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 34.5 | 2 | 0.02
Indirect contribution | C1 | W | 245.2 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 3.94
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 7.88 (0.04 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)