## 60K ID (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
EER | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 12.68 | 12.69 | 12.68 | 12.68 | 12.68 | 12.68 | 12.67
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
60K INDOOR
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
Entering DB | ℃ | 20.93 | 20.82 | 20.88 | 20.92 | 20.96 | 20.99 | 21.01
Entering WB | ℃ | 17.55 | 17.03 | 17.35 | 17.62 | 17.71 | 17.78 | 17.79
Entering RH | % | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71
Leaving DB | ℃ | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.54
Leaving WB | ℃ | 19.77 | 19.74 | 19.75 | 19.76 | 19.77 | 19.79 | 19.81
Leaving RH | % | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1
Ehthalpy (Ent) | kcal/kg' | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48
Enthalpy (Lev) | kcal/kg' | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145
Humidity Ratio (Ent) | kg/kg' | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324
Humidity Ratio (Lev) | kg/kg' | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083
Specific Heat (Lev) | kcal/kg℃ | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246
Specific Volume (Lev) | ㎥/kg | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256
Static Pressure | mmAq | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27
Barometric Pressure | mmHg | 767.58 | 767.66 | 767.54 | 767.55 | 767.58 | 767.58 | 767.56
Nozzle Inlet Temp. | ℃ | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.54
Nozzle 100/100/125/125 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## ID 1
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  | TCL |  |  | Request No.
Maker |  | TCL |  |  | Test Date |  | 2023-08-08
Test Method |  | Cooling |  |  | File Name |  | P-20230808 02-24-25.psy
Rated Capacity |  | 18,000 Btu/h |  |  | ID Model Name
Rated Power |  | 0 W |  |  | ID Serial Number
Power Source |  | 1P2W / 220 V / 60 Hz |  |  | OD Model Name
Observer |  | Bruno Moretti / RSS |  |  | OD Serial Number
Refrigerant |  | R410A - g |  |  | Exp. Device
ID Entering DB/WB |  | 27 / 19 ℃ |  |  | OD Entering DB/WB |  | 29 / 19 ℃
- |  |  |  |  | -
Note
TCL - 18k - Split - Fixa- Standard - 69983
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
Total Capacity | Btu/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
EER | Btu/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | m³/min | 12.68 | 12.69 | 12.68 | 12.68 | 12.68 | 12.68 | 12.67
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
30K INDOOR
Capacity | Btu/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Air Flow (Lev) | m³/min | 12.68 | 12.69 | 12.68 | 12.68 | 12.68 | 12.68 | 12.67
Entering DB | ℃ | 27 | 27 | 26.99 | 27 | 27 | 27 | 26.99
Entering WB | ℃ | 19 | 19 | 19 | 18.98 | 19 | 19 | 19
Entering RH | % | 46.78 | 46.77 | 46.81 | 46.71 | 46.79 | 46.8 | 46.79
Leaving DB | ℃ | 13.06 | 13.06 | 13.06 | 13.05 | 13.05 | 13.05 | 13.05
Leaving WB | ℃ | 12.1 | 12.11 | 12.11 | 12.1 | 12.1 | 12.11 | 12.1
Leaving RH | % | 89.76 | 89.74 | 89.74 | 89.73 | 89.79 | 89.8 | 89.77
Ehthalpy (Ent) | kJ/kg' | 53.445 | 53.443 | 53.46 | 53.406 | 53.458 | 53.459 | 53.447
Enthalpy (Lev) | kJ/kg' | 34.114 | 34.121 | 34.124 | 34.092 | 34.114 | 34.119 | 34.113
Humidity Ratio (Ent) | kg/kg' | 0.010308 | 0.010306 | 0.010314 | 0.010292 | 0.010312 | 0.010313 | 0.010309
Humidity Ratio (Lev) | kg/kg' | 0.00831 | 0.008311 | 0.008312 | 0.008304 | 0.008311 | 0.008313 | 0.00831
Specific Heat (Lev) | kJ/kg'-°C | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213
Specific Volume (Lev) | ㎥/kg | 0.8135 | 0.8134 | 0.8136 | 0.8135 | 0.8135 | 0.8135 | 0.8135
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 47.84 | 47.92 | 47.83 | 47.86 | 47.82 | 47.81 | 47.78
Heat Leakage | Btu/h | 165.9 | 165.9 | 165.9 | 166 | 166 | 166 | 165.9
Drain Weight | kg/h | 1.87 | 1.87 | 1.87 | 1.86 | 1.87 | 1.87 | 1.87
Lantent Heat | Btu/h | 4358.4 | 4358.5 | 4367.6 | 4339.7 | 4364.2 | 4362.7 | 4357.9
Sensible Heat | Btu/h | 12945.8 | 12952.4 | 12938.9 | 12953.5 | 12947.6 | 12943.6 | 12938.4
Sensible Heat Ratio | % | 74.81 | 74.82 | 74.76 | 74.91 | 74.79 | 74.79 | 74.8
Barometric Pressure | mmHg | 767.58 | 767.66 | 767.54 | 767.55 | 767.58 | 767.58 | 767.56
Nozzle Inlet Temp. | ℃ | 13.06 | 13.06 | 13.06 | 13.05 | 13.05 | 13.05 | 13.05
Nozzle 50/60/80/100 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY #1 | [6 empty] | LABELO

## I3 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
EER | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 12.68 | 12.69 | 12.68 | 12.68 | 12.68 | 12.68 | 12.67
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## I4 (hidden)
PSYCHROMETRIC CALORIMETER INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | -
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
EER | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Total Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Air Flow | ㎥/min | 12.68 | 12.69 | 12.68 | 12.68 | 12.68 | 12.68 | 12.67
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W1 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
INDOOR 1
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 31.6
Entering DB | ℃ | 20.93 | 20.82 | 20.88 | 20.92 | 20.96 | 20.99 | 21.01
Entering WB | ℃ | 17.55 | 17.03 | 17.35 | 17.62 | 17.71 | 17.78 | 17.79
Entering RH | % | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71
Leaving DB | ℃ | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.54
Leaving WB | ℃ | 19.77 | 19.74 | 19.75 | 19.76 | 19.77 | 19.79 | 19.81
Leaving RH | % | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1 | 92.1
Ehthalpy (Ent) | kcal/kg' | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48 | 53.48
Enthalpy (Lev) | kcal/kg' | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145 | 41.145
Humidity Ratio (Ent) | kg/kg' | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324 | 0.010324
Humidity Ratio (Lev) | kg/kg' | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083 | 0.010083
Specific Heat (Lev) | kcal/kg℃ | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246 | 1.0246
Specific Volume (Lev) | ㎥/kg | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256 | 0.8256
Static Pressure | mmAq | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27 | 95.27
Barometric Pressure | mmHg | 767.58 | 767.66 | 767.54 | 767.55 | 767.58 | 767.58 | 767.56
Nozzle Inlet Temp. | ℃ | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.53 | 20.54
Nozzle 110/140/165/200 | - | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/- | -/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W2 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
INDOOR 2
Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Air Flow (Lev) | ㎥/min | 12.68 | 12.69 | 12.68 | 12.68 | 12.68 | 12.68 | 12.67
Entering DB | ℃ | 27 | 27 | 26.99 | 27 | 27 | 27 | 26.99
Entering WB | ℃ | 19 | 19 | 19 | 18.98 | 19 | 19 | 19
Entering RH | % | 46.78 | 46.77 | 46.81 | 46.71 | 46.79 | 46.8 | 46.79
Leaving DB | ℃ | 13.06 | 13.06 | 13.06 | 13.05 | 13.05 | 13.05 | 13.05
Leaving WB | ℃ | 12.1 | 12.11 | 12.11 | 12.1 | 12.1 | 12.11 | 12.1
Leaving RH | % | 89.76 | 89.74 | 89.74 | 89.73 | 89.79 | 89.8 | 89.77
Ehthalpy (Ent) | kcal/kg' | 53.445 | 53.443 | 53.46 | 53.406 | 53.458 | 53.459 | 53.447
Enthalpy (Lev) | kcal/kg' | 34.114 | 34.121 | 34.124 | 34.092 | 34.114 | 34.119 | 34.113
Humidity Ratio (Ent) | kg/kg' | 0.010308 | 0.010306 | 0.010314 | 0.010292 | 0.010312 | 0.010313 | 0.010309
Humidity Ratio (Lev) | kg/kg' | 0.00831 | 0.008311 | 0.008312 | 0.008304 | 0.008311 | 0.008313 | 0.00831
Specific Heat (Lev) | kcal/kg℃ | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213 | 1.0213
Specific Volume (Lev) | ㎥/kg | 0.8135 | 0.8134 | 0.8136 | 0.8135 | 0.8135 | 0.8135 | 0.8135
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 47.84 | 47.92 | 47.83 | 47.86 | 47.82 | 47.81 | 47.78
Heat Leakage | kcal/h | 165.9 | 165.9 | 165.9 | 166 | 166 | 166 | 165.9
Drain Weight | kg/h | 1.87 | 1.87 | 1.87 | 1.86 | 1.87 | 1.87 | 1.87
Lantent Heat | kcal/h | 4358.4 | 4358.5 | 4367.6 | 4339.7 | 4364.2 | 4362.7 | 4357.9
Sensible Heat | kcal/h | 12945.8 | 12952.4 | 12938.9 | 12953.5 | 12947.6 | 12943.6 | 12938.4
Sensible Heat Ratio | % | 74.81 | 74.82 | 74.76 | 74.91 | 74.79 | 74.79 | 74.8
Barometric Pressure | mmHg | 767.58 | 767.66 | 767.54 | 767.55 | 767.58 | 767.58 | 767.56
Nozzle Inlet Temp. | ℃ | 13.06 | 13.06 | 13.06 | 13.05 | 13.05 | 13.05 | 13.05
Nozzle 60/80/110/125 | - | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/- | -/O/O/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W3 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
INDOOR 3
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/- | -/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## W4 (hidden)
WATER TO AIR TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
- |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Total Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Total Capacity | kcal/h | 17304.2 | 17310.9 | 17306.5 | 17293.2 | 17311.8 | 17306.4 | 17296.3
Total Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Net Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
EER Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
INDOOR 4
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air Flow (Lev) | ㎥/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Entering RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving DB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving WB | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Leaving RH | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ehthalpy (Ent) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Enthalpy (Lev) | kcal/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Ent) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (Lev) | kg/kg' | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Heat (Lev) | kcal/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Specific Volume (Lev) | ㎥/kg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Static Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Diff. Pressure | mmAq | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Leakage | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Drain Weight | kg/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lantent Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Heat Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barometric Pressure | mmHg | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nozzle 225/250/300/300/300 | - | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/- | -/-/-/-/-/-
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## G (hidden)
WATER TO WATER TEST INSPECTION DATA | [9 empty] | a
Client |  |  |  |  | Request No.
Maker |  |  |  |  | Test Date
Test Method |  |  |  |  | File Name
Rated Capacity |  |  |  |  | ID Model Name
Rated Power |  |  |  |  | ID Serial Number
Power Source |  |  |  |  | OD Model Name
Observer |  |  |  |  | OD Serial Number
Refrigerant |  |  |  |  | Exp. Device
ID Entering DB/WB |  |  |  |  | OD Entering DB/WB
LS Temp/Flow Rate |  |  |  |  | HS Temp/Flow Rate
Note
Test Results |  | Average | 5 min | 10 min | 15 min | 20 min | 25 min | 30 min | 35 min
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Effective Power Input | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc | kcal/hW | 13.02 | 13.028 | 13.023 | 13.013 | 13.025 | 13.02 | 13.01
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Heat Balance | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Balance Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capacity Ratio | % | 96.13 | 96.17 | 96.15 | 96.07 | 96.18 | 96.15 | 96.09
Effective Power Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
COPc Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Total Current Ratio | % | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Input | W | 1329 | 1328.8 | 1328.9 | 1329 | 1329.1 | 1329.2 | 1329.4
Voltage | V | 219.9 | 219.9 | 219.9 | 219.9 | 219.8 | 219.8 | 219.8
Current | A | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24 | 6.24
Frequency | Hz | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99 | 59.99
Power Factor | % | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9 | 96.9
INDOOR
Entering DB | ℃ | 20.93 | 20.82 | 20.88 | 20.92 | 20.96 | 20.99 | 21.01
Entering WB | ℃ | 17.55 | 17.03 | 17.35 | 17.62 | 17.71 | 17.78 | 17.79
Entering RH | % | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71 | 46.71
Barometric Pressure | mmHg | 767.58 | 767.66 | 767.54 | 767.55 | 767.58 | 767.58 | 767.56
OUTDOOR
Entering DB | ℃ | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Entering WB | ℃ | 18.99 | 18.99 | 18.99 | 19 | 18.99 | 18.99 | 19
Entering RH | % | 38.34 | 38.29 | 38.32 | 38.38 | 38.34 | 38.34 | 38.35
Entering Dew Point | ℃ | 13.48 | 13.45 | 13.46 | 13.49 | 13.48 | 13.48 | 13.5
LOAD SIDE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEAT SOURCE
Net Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity | kcal/h | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Rate | L/min | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Inlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Outlet Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Average Temp. | ℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Density | kg/㎥ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Specific Heat | kJ/kg℃ | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Diff. Pressure | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Power | W | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE
Pressure 1 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 2 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 3 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
Pressure 4 | bar | -999 | -999 | -999 | -999 | -999 | -999 | -999
PSY - MULTI | [6 empty] | LABELO

## TC-60K ID (hidden)
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-30K ID
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
30K INDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## TC-60K OD
THERMOCOUPLE INSPECTION DATA SHEET | [9 empty] | a
Test Results |  | Average | 10 min | 20 min | 30 min | 40 min | 50 min | 60 min | --
60K OUTDOOR - TC
01: | ℃ | -- | -- | -- | -- | -- | -- | --
02: | ℃ | -- | -- | -- | -- | -- | -- | --
03: | ℃ | -- | -- | -- | -- | -- | -- | --
04: | ℃ | -- | -- | -- | -- | -- | -- | --
05: | ℃ | -- | -- | -- | -- | -- | -- | --
06: | ℃ | -- | -- | -- | -- | -- | -- | --
07: | ℃ | -- | -- | -- | -- | -- | -- | --
08: | ℃ | -- | -- | -- | -- | -- | -- | --
09: | ℃ | -- | -- | -- | -- | -- | -- | --
10: | ℃ | -- | -- | -- | -- | -- | -- | --
11: | ℃ | -- | -- | -- | -- | -- | -- | --
12: | ℃ | -- | -- | -- | -- | -- | -- | --
13: | ℃ | -- | -- | -- | -- | -- | -- | --
14: | ℃ | -- | -- | -- | -- | -- | -- | --
15: | ℃ | -- | -- | -- | -- | -- | -- | --
16: | ℃ | -- | -- | -- | -- | -- | -- | --
17: | ℃ | -- | -- | -- | -- | -- | -- | --
18: | ℃ | -- | -- | -- | -- | -- | -- | --
19: | ℃ | -- | -- | -- | -- | -- | -- | --
20: | ℃ | -- | -- | -- | -- | -- | -- | --
21: | ℃ | -- | -- | -- | -- | -- | -- | --
22: | ℃ | -- | -- | -- | -- | -- | -- | --
23: | ℃ | -- | -- | -- | -- | -- | -- | --
24: | ℃ | -- | -- | -- | -- | -- | -- | --
25: | ℃ | -- | -- | -- | -- | -- | -- | --
26: | ℃ | -- | -- | -- | -- | -- | -- | --
27: | ℃ | -- | -- | -- | -- | -- | -- | --
28: | ℃ | -- | -- | -- | -- | -- | -- | --
29: | ℃ | -- | -- | -- | -- | -- | -- | --
30: | ℃ | -- | -- | -- | -- | -- | -- | --
PSY #1 | [6 empty] | LABELO

## Unc_60K (C) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s |  | 2
Specific enthalpy of air entering the indoor side | ha1 | J/kg |  | 2
Specific enthalpy of air leaving the indoor side | ha2 | J/kg |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | C1 | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_60K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (C)
■ Uncertainty Analysis
Application No.
Model Name
Test Date |  | 2023-08-08 04:10
Test Time |  | 1:45
Operator |  | Bruno Moretti / RSS
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty |  | 7.57%
Relative expanded uncertainty |  | 0.04%
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Airflow | qvi | m3/s | 0.01 | 2 | 2.4
Specific enthalpy of air entering the indoor side | ha1 | J/kg | 801.7 | 2 | 2.07
Specific enthalpy of air leaving the indoor side | ha2 | J/kg | 511.7 | 2 | 1.32
Air dry bulb temperature | T | K | 0.2 | 2 | 0.03
Atmospheric pressure | p | Pa | 1023.36 | 2 | 0.51
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa | 32.4 | 2 | 0.02
Indirect contribution | C1 | W | 259.6 | 1 | 1.5
Relative combined standard uncertainty |  |  |  |  | 3.78
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2 |  |  |  |  | 7.57 (0.04 %)
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)

## Unc_30K (H) (hidden)
■ Uncertainty Analysis
Application No.
Model Name
Test Date
Test Time
Operator
Uncertainty |  | ISO/TS 16491:2012
Expanded uncertainty
Relative expanded uncertainty
Coverage factor |  | k = 2
Input quantity Source of Uncertainty |  | Unit | Value from calibration certificate or actual value | Divisor | Calculation of relative standard uncertainy(%)
Indoor air volume flow rate | qvi | m3/s |  | 2
Specific heat of moist air entering the indoor side | Cpa2 | J/kg℃ |  | 2
Temperature of air leaving the indoor side, drybulb | ta2 | ℃ |  | 2
Specific heat of moist air entering the indoor side | Cpa1 | J/kg℃ |  | 2
Temperature of air entering the indoor side, dry bulb | ta1 | ℃ |  | 2
Air dry bulb temperature | T | K |  | 2
Atmospheric pressure | p | Pa |  | 2
Water vapour partial pressure at wet bulb temperature Tw | pw | Pa |  | 2
Indirect contribution | Ci | W |  | 1
Relative combined standard uncertainty
Relative expanded uncertainty(Relative expanded uncertainty (%)) Converge factor k=2
TEQP-26-07-3 | LABELO BRAZIL |  |  |  | A4(210mm*297mm)